## Statistics PM
AREA | Week 1 (1 March To 4 March)
| EQUIPMENT | Schedule PM | PM done
PV | PV INSPECTION-D | 4 | 4
PV | WEATHER MONITORING STATION-D | 4 | 4
PV | ARCS ROBOT OPERATION-D | 4 | 4
PVSS | DAILY SUBSTATION INSPECTION-D | 4 | 4
PVSS | SUBSTATION CLEANING-D | 4 | 4
PVSS | POWER TRANSFORMER DGA TEST-D | 4 | 4
PVSS | CCTV INSPECTION-D | 4 | 4
PVSS | EDG TEST RUN-W SS | 1 | 1
PVSS | EDG TEST RUN-W SB | 1 | 1
PVSS | SVG COOLING UNIT DUST CLEANING-W | 4 | 4
PV | WEATHER MONITORING STATION-W | 9 | 9
PV | SCB'S MAINTENANCE-HY | 8 | 4
PV | ARCS ROBOT MAINTENANCE-HY | 83 | 83
PV | POWER STATION MAINTENANCE-HY | 8 | 4
PVSS | WATER PUMPING SYSTEM MAINTENANCE-M | 3 | 3
HSE | FIRE EXTINGUISHER INSPECTION-M | All | All
PVSS | ALL FACILITY LIGHTNING AND POWER SYSTEM-M | 4 | 4
| TOTAL | 149 | 141
| COMPLIANCE SCORE | 94.63%
| PENDING | 5.369%
AREA | Week 2 (05 March To 11 March)
| EQUIPMENT | Schedule PM | PM done
PV | PV INSPECTION-D | 7 | 7
PV | WEATHER MONITORING STATION-D | 7 | 7
PV | ARCS ROBOT OPERATION-D | 7 | 7
PVSS | DAILY SUBSTATION INSPECTION-D | 7 | 7
PVSS | SUBSTATION CLEANING-D | 7 | 7
PVSS | POWER TRANSFORMER DGA TEST-D | 7 | 7
PVSS | CCTV INSPECTION-D | 7 | 7
PVSS | EDG TEST RUN-W SS | 1 | 1
PVSS | EDG TEST RUN-W SB | 1 | 1
PVSS | SVG COOLING UNIT DUST CLEANING-W | 6 | 6
PV | WEATHER MONITORING STATION-W | 9 | 9
PV | SCB'S MAINTENANCE-HY | 14 | 7
PV | ARCS ROBOT MAINTENANCE-HY | 140 | 140
PV | POWER STATION MAINTENANCE-HY | 14 | 7
HSE | EMERGENCY RESPONSE KIT INSPECTION-M | All | All
HSE | TOOLS AAND EQUIPMENT INSPECTION-M | All | All
General | FIRE ALARM SYSTEM INSPECTION-M | 3 | 3
PVSS | FIRE FIGHTNING SYSTEM INSPECTION-M | 1 | 1
General | MAIN GATE AND ROAD BLOCKERS MAINTENANCE-M | 2 | 2
PVSS | BATTERY BANK MAINTENANCE-M | 2 | 2
| TOTAL | 242 | 228
| COMPLIANCE SCORE | 94.21%
| PENDING | 5.785%
Week 3 (12 March To 18 March)
| EQUIPMENT | Schedule PM | PM done
PV | PV INSPECTION-D | 7 | 4
PV | WEATHER MONITORING STATION-D | 7 | 4
PV | ARCS ROBOT OPERATION-D | 7 | 2
PVSS | DAILY SUBSTATION INSPECTION-D | 7 | 3
PVSS | SUBSTATION CLEANING-D | 7 | 3
PVSS | POWER TRANSFORMER DGA TEST-D | 7 | 3
PVSS | CCTV INSPECTION-D | 7 | 3
PVSS | EDG TEST RUN-W SS | 1
PVSS | EDG TEST RUN-W SB | 1
PVSS | SVG COOLING UNIT DUST CLEANING-W | 6 | 2
PV | WEATHER MONITORING STATION-W | 9
PV | SCB'S MAINTENANCE-HY | 14 | 3
PV | ARCS ROBOT MAINTENANCE-HY | 142 | 60
PV | POWER STATION MAINTENANCE-HY | 14 | 3
PVSS | HVAC FILTER CLEANING-M | 1 | 1
PVSS | HVAC MAINTENANCE-Q | 3
PV | POWER STATION MAINTENANCE-M | 70
HSE | HSE PPE INSPECTION-M | ALL
General | ASPHALT ROAD CLEANING-M | All
PV | ARCS ROBOTS CHECKING-M | All
| TOTAL | 310 | 91
| COMPLIANCE SCORE | 29.35%
| PENDING | 70.65%
Week 4 (19 March To 25 March)
| EQUIPMENT | Schedule PM | PM done
PV | PV INSPECTION-D
PV | WEATHER MONITORING STATION-D
PV | ARCS ROBOT OPERATION-D
PVSS | DAILY SUBSTATION INSPECTION-D
PVSS | SUBSTATION CLEANING-D
PVSS | POWER TRANSFORMER DGA TEST-D
PVSS | CCTV INSPECTION-D
PVSS | EDG TEST RUN-W SS
PVSS | EDG TEST RUN-W SB
PVSS | SVG COOLING UNIT DUST CLEANING-W
PV | WEATHER MONITORING STATION-W
PV | SCB'S MAINTENANCE-HY
PV | ARCS ROBOT MAINTENANCE-HY
PV | POWER STATION MAINTENANCE-HY
PVSS | HVAC FILTER CLEANING-M
PV | POWER STATION MAINTENANCE-M
PV | PERIMETER FENCE MAINTENANCE-M
PV | PERMIMETER LIGHTNING SYSTEM MAINTENANCE-M
PVSS | HVAC MAINTENANCE-Q
TOTAL
| COMPLIANCE SCORE | #DIV/0!
| PENDING | #DIV/0!
Week 5 (26 March To 31 March)
| EQUIPMENT | Schedule PM | PM done
PV | PV INSPECTION-D
PV | WEATHER MONITORING STATION-D
PV | ARCS ROBOT OPERATION-D
PVSS | DAILY SUBSTATION INSPECTION-D
PVSS | SUBSTATION CLEANING-D
PVSS | POWER TRANSFORMER DGA TEST-D
PVSS | CCTV INSPECTION-D
PVSS | EDG TEST RUN-W SS
PVSS | EDG TEST RUN-W SB
PVSS | SVG COOLING UNIT DUST CLEANING-W
PV | WEATHER MONITORING STATION-W
PV | SCB'S MAINTENANCE-HY
PV | ARCS ROBOT MAINTENANCE-HY
PV | POWER STATION MAINTENANCE-HY
PVSS | HVAC FILTER CLEANING-M
PV | POWER STATION MAINTENANCE-M
PVSS | HVAC MAINTENANCE-Q
PVSS | WEATHER MONITORING STATION-M
TOTAL
COMPLIANCE SCORE
PENDING
March Month
| EQUIPMENT | Schedule PM | PM done
TOTAL
| COMPLIANCE SCORE | #DIV/0!
| PENDING | #DIV/0!

## Statistics CM
Week 1 (1 March To 4 March)
EQUIPMENT | Schedule CM | CM Done
INVERTERS | 0 | 0
STRINGS | 0 | 0
TRACKERS | 35 | 32
COMBINER BOXES | 1 | 1
MV Joints | 3 | 3
SVG Faulty | 4 | 4
WMS Communication Issue | 1 | 0
SST 1 Termination failure | 1 | 1
GT 1 Oil seepage | 1 | 0
TOTAL | 46 | 41
COMPLIANCE SCORE | 89.13%
PENDING | 10.87%
Week 2 (05 March To 11 March)
EQUIPMENT | Schedule CM | CM Done
INVERTERS | 4 | 4
STRINGS | 3 | 3
TRACKERS | 62 | 55
COMBINER BOXES | 1 | 1
MV Joints | 1 | 1
WMS Communication Issue | 1 | 0
GT 1 Oil seepage | 1 | 0
TOTAL | 73 | 64
COMPLIANCE SCORE | 87.67%
PENDING | 12.33%
Week 3 (12 March To 18 March)
EQUIPMENT | Schedule CM | CM Done
INVERTERS | 1 | 1
STRINGS | 1 | 1
TRACKERS | 27 | 21
COMBINER BOXES | 5 | 5
MV Joints | 2 | 2
WMS Communication Issue | 1 | 0
GT 1 Oil seepage | 1 | 0
SVG | 2 | 1
TOTAL | 40 | 31
COMPLIANCE SCORE | 77.5%
PENDING | 22.5%
Week 4 (19 March To 25 March)
EQUIPMENT | Schedule CM | CM Done
TOTAL | 0 | 0
COMPLIANCE SCORE | #DIV/0!
PENDING | #DIV/0!
Week 5 (26 March To 31 March)
EQUIPMENT | Schedule CM | CM Done
TOTAL | 0 | 0
COMPLIANCE SCORE | #DIV/0!
PENDING | #DIV/0!
March Month
EQUIPMENT | Schedule CM | CM Done
TOTAL | 306 | 297
COMPLIANCE SCORE | 97.06%
PENDING | 2.941%

## PM Tracing
Daily Maintenance
Task Description | Description | 2026-03-01 |  | 2026-03-02 |  | 2026-03-03 |  | 2026-03-04 |  | 2026-03-05 |  | 2026-03-06 |  | 2026-03-07 |  | 2026-03-08 |  | 2026-03-09 |  | 2026-03-10 |  | 2026-03-11 |  | 2026-03-12 |  | 2026-03-13 |  | 2026-03-14 |  | 2026-03-15 |  | 2026-03-16 |  | 2026-03-17 |  | 2026-03-18 |  | 2026-03-19 |  | 2026-03-20 |  | 2026-03-21 |  | 2026-03-22 |  | 2026-03-23 |  | 2026-03-24 |  | 2026-03-25 |  | 2026-03-26 |  | 2026-03-27 |  | 2026-03-28 |  | 2026-03-29 |  | 2026-03-30 |  | 2026-03-31
|  | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist
PV Inspection-D | 3 | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done
Weather Monitoring Station-D | cleaning pyranometers sensors | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done
ARCS Robot Operation-D | 100% of the robots operation | 707 |  | 778 |  | 781 |  | 764 |  | 559 |  | 842 |  | 774 |  | 641 |  | 776 |  | 792 |  | 582 |  | 434 |  | 839 |  | 0
Daily Substation Inspection-D | visual inspection of SS | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done
Substation Cleaning -D | All the buildings + bathrooms (no need checklist ) | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  | Done |  |  |  | Done |  | Done
Power Transformer DGA Test-D | DGA test of 6 PT | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done
CCTV Inspection-D | MVPs CCTV | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done | Done
Weekly Maintenance
Task Description | Description | week 1 |  | week 2 |  | week 3 |  | week 4
|  | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist
EDG Test Run-W SS | test run less than 10 minuts | 2026.03.03 | Done | 2026.03.09 | Done
EDG Test Run-W SB | test run less than 10 minuts | 2026.03.03 | Done | 2026.03.09 | Done
|  | Week 1 | [11 empty] | Week 2 | [11 empty] | Week 3 | [11 empty] | Week 4 | [11 empty] | Week 5
Task Description | Description | SVG 1 |  | SVG 2 |  | SVG 3 |  | SVG 4 |  | SVG 5 |  | SVG 6 |  | SVG 1 |  | SVG 2 |  | SVG 3 |  | SVG 4 |  | SVG 5 |  | SVG 6 |  | SVG 1 |  | SVG 2 |  | SVG 3 |  | SVG 4 |  | SVG 5 |  | SVG 6 |  | SVG 1 |  | SVG 2 |  | SVG 3 |  | SVG 4 |  | SVG 5 |  | SVG 6 |  | SVG 6 |  | SVG 1
|  | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist | Performing Date | Checklist
SVG Cooling Unit Dust Cleaning-W | cleaning of cooling system for 6 SVGs |  |  | 2026.03.01 | Done | 2026.03.02 | Done | 2026.03.03 | Done | 2026.03.04 | Done | 2026.03.05 | Done | 2026.03.08 | Done | 2026.03.08 | Done | 2026.03.09 | Done | 2026.03.10 | Done | 2026.03.11 | Done |  |  | 2026.03.14 | Done | 2026.03.15 | Done | [6 empty] | 2026.03.12 | Done
Task Description | Description | week 1 |  | week 2 |  | week 3 |  | week 4
|  | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist
Weather Monitoring Station-W | Cleaning of Module and Ventilation hod | 2026.03.03 | Done | 2026.03.10 | Done
Monthly Maintenance
Maintenance Description | Description | Block Number | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist
POWER STATION MAINTENANCE-M | Visual Inspection of all MVPS + RMU filter Cleaning + UPS Filter Cleaning + PD Panel filter Cleaning + Follow checklist points | 1 |  |  | 34 |  |  |  | 67 |  |  |  | 100
|  | 2 |  |  | 35 |  |  |  | 68 |  |  |  | 101
|  | 3 |  |  | 36 |  |  |  | 69 |  |  |  | 102
|  | 4 |  |  | 37 |  |  |  | 70 |  |  |  | 103
|  | 5 |  |  | 38 |  |  |  | 71 |  |  |  | 104
|  | 6 |  |  | 39 |  |  |  | 72 |  |  |  | 105
|  | 7 |  |  | 40 |  |  |  | 73 |  |  |  | 106
|  | 8 |  |  | 41 |  |  |  | 74 |  |  |  | 107
|  | 9 |  |  | 42 |  |  |  | 75 |  |  |  | 108
|  | 10 |  |  | 43 |  |  |  | 76 |  |  |  | 109
|  | 11 |  |  | 44 |  |  |  | 77 |  |  |  | 110
|  | 12 |  |  | 45 |  |  |  | 78 |  |  |  | 111
|  | 13 |  |  | 46 |  |  |  | 79 |  |  |  | 112
|  | 14 |  |  | 47 |  |  |  | 80 |  |  |  | 113
|  | 15 |  |  | 48 |  |  |  | 81 |  |  |  | 114
|  | 16 |  |  | 49 |  |  |  | 82 |  |  |  | 115
|  | 17 |  |  | 50 |  |  |  | 83 |  |  |  | 116
|  | 18 |  |  | 51 |  |  |  | 84 |  |  |  | 117
|  | 19 |  |  | 52 |  |  |  | 85 |  |  |  | 118
|  | 20 |  |  | 53 |  |  |  | 86 |  |  |  | 119
|  | 21 |  |  | 54 |  |  |  | 87 |  |  |  | 120
|  | 22 |  |  | 55 |  |  |  | 88 |  |  |  | 121
|  | 23 |  |  | 56 |  |  |  | 89 |  |  |  | 122
|  | 24 |  |  | 57 |  |  |  | 90 |  |  |  | 123
|  | 25 |  |  | 58 |  |  |  | 91 |  |  |  | 124
|  | 26 |  |  | 59 |  |  |  | 92 |  |  |  | 125
|  | 27 |  |  | 60 |  |  |  | 93 |  |  |  | 126
|  | 28 |  |  | 61 |  |  |  | 94 |  |  |  | 127
|  | 29 |  |  | 62 |  |  |  | 95 |  |  |  | 128
|  | 30 |  |  | 63 |  |  |  | 96 |  |  |  | 129
|  | 31 |  |  | 64 |  |  |  | 97 |  |  |  | 130
|  | 32 |  |  | 65 |  |  |  | 98 |  |  |  | 131
|  | 33 |  |  | 66 |  |  |  | 99 |  |  |  | 132
HVAC Cleaning - M | Filter Cleaning + General Cleaning | Unit Name | Location | Performing Date | Basement Supply fan | Performing Date | Basement Exhaust fan | Performing Date | Fresh Air Supply Fan | Location | Performing Date | Exhaust Fan | Location | Performing Date | Toilets Exhaust | Location | Performing Date | Split AC | Location | Performing Date
|  | 1A | Switchgear room |  | VSF 1-01 |  | VEF 1-01 |  | WSF 1 | Hazrdous room 1 |  | WEF 1 | Pump Room |  | WEF 1 | O&M building |  | Split AC | Pump room
|  | 1B | Switchgear room |  | VSF 1-02 |  | VEF 1-02 |  | WSF 2 | Hazrdous room 2 |  | WEF 2 | Pump Room |  | WEF 2 | O&M building |  | Split AC 1 | O&M Store
|  | 2A | Control Building |  | VSF 2-01 |  | VEF 2-01 |  | WSF 1 | Warehouse room 1 |  | WEF 1 | Warehouse room 1 |  | WEF 5 | O&M building |  | Split AC 2 | O&M Store
|  | 2B | Control Building |  | VSF 2-02 |  | VEF 2-02 |  | WSF 2 | Warehouse room 1 |  | WEF 2 | Warehouse room 1 |  | WEF 2-01 | Control building |  | Split AC 1 | Security building
|  | 3A | O&M Building | [5 empty] | WSF 3 | Warehouse room 2 |  | WEF 3 | Warehouse room 2 |  |  |  |  | Split AC 2 | Security building
|  | 3B | O&M Building | [5 empty] | WSF 4 | Warehouse room 2 |  | WEF 4 | Warehouse room 2 |  |  |  |  | Split AC 3 | Security building
|  | 4A | GIS Building | 2026.03.12 | [7 empty] | WEF 2-02 | Fire Fighting room |  |  |  |  | Split AC 4 | Security building
|  | 4B | GIS Building | [14 empty] | Split AC 5 | Security building
[18 empty] | Split AC 6 | Security building
[18 empty] | Split AC 7 | Security building
[18 empty] | Split AC 8 | Security building
[18 empty] | Split AC 9 | Security building
[18 empty] | Split AC 10 | Security building
Task Description | Description | Date (xxxx)
|  | Performed | Checklist
Weather Monitoring Station-M | Cleaining the sensors + Fans + dust IQ
Perimeter fence Maintenance -M | General Inspection
Asphalt Road Cleaning-M | Main gate to substation and substation Road
Battery Bank Maintenance-M | General Inspection + Cleaning | 2026.03.07 | Done
ARCS Robot Checking-M | From SCADA
Perimeter Lightning System Maintenance-M | Check visually all lights for any damage or faulty
HSE PPE Inspection-M | All PPE's inspect and give colour code
Emergency response kit Inspection-M | Walkie-Talkie, First aid kit, Electrical Rescue kit | 2026.03.11 | Done
Tools and Equipment Inspection-M | All tools and equipment inspection and colour coding | 2026.03.11 | Done
Fire Extinguisher Inspection-M | All SS and MVPS fire extinguishers | 2026.03.03 | Done
Fire Alarm system Inspection-M | All SS Fire panel and DB's Inspection | 2026.03.10 | Done
Fire Fightning System Inspection-M | All fire fightning pumps inspection
Main gate and Road Blocker Maintenance-M | Cleaning + Checking if any issue | 2026.03.05 | Done
Water Pumping System Maintenance-M | Cleaning + Checking + Running | O&M Building |  | Control Building |  | Warehouse Building
|  | Performed | Date | Performed | Date | Performed | Date
|  | Done | 2026.03.03 | Done | 2026.03.03 | Done | 2026.03.03
All Facility Lightning and Power System-M | Checking and Rectification if any faulty | Control Building |  | O&M Building |  | GIS Building |  | Substation Indoor Lightning
|  | Performed | Date | Performed | Date | Performed | Date | Performed | Date
|  | Done | 2026.03.03 | Done | 2026.03.03 | Done | 2026.03.03 | Done | 2026.03.03
POWER STATION AND SCB MAINTENANCE-HY | Checking + Cleaning + Tightning of screws and cables + Follow checklist | Block Number | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist | Block Number | Status | Performing Date | Checklist
|  | 1 |  |  | 34 |  | 2026-03-15 |  | 67 |  |  |  | 100 | Done | 2026.02.19 | Done
|  | 2 |  |  | 35 |  |  |  | 68 | Done | 2026.03.01 | Done | 101 | Done | 2026.01.30 | Done
|  | 3 |  |  | 36 |  |  |  | 69 |  |  |  | 102 | Done | 2026.01.14 | Done
|  | 4 |  |  | 37 |  |  |  | 70 | Done | 2026.02.07 | Done | 103 | Done | 2026.01.18 | Done
|  | 5 | 2026.03.04 | Done | 38 | Done | 2026.02.02 | Done | 71 | Done | 2026.01.29 | Done | 104
|  | 6 |  |  | 39 |  |  |  | 72 | Done | 2026.02.13 | Done | 105 | Done | 2026.02.24 | Done
|  | 7 | 2026.03.09 | Done | 40 |  |  |  | 73 |  |  |  | 106 | Done | 2026.03.02 | Done
|  | 8 |  |  | 41 |  |  |  | 74 | Done | 2026.01.22 | Done | 107
|  | 9 |  |  | 42 |  |  |  | 75 | Done | 2026.02.06 | Done | 108
|  | 10 |  |  | 43 |  |  |  | 76 | Done | 2026.02.22 | Done | 109
|  | 11 |  |  | 44 | Done | 2026.02.14 | Done | 77 |  |  |  | 110 | Done | 2026.02.08 | Done
|  | 12 |  |  | 45 |  |  |  | 78 |  |  |  | 111
|  | 13 |  |  | 46 | Done | 2026.02.01 | Done | 79 |  |  |  | 112 | Done | 2026.01.26 | Done
|  | 14 |  |  | 47 | Done | 2026.02.03 | Done | 80 |  |  |  | 113
|  | 15 |  |  | 48 |  |  |  | 81 |  |  |  | 114 | Done | 2026.02.17 | Done
|  | 16 |  |  | 49 |  |  |  | 82 | Done | 2026.02.27 | Done | 115
|  | 17 |  |  | 50 |  |  |  | 83 |  |  |  | 116 | Done | 2026.01.15 | Done
|  | 18 | 2026.03.10 | Done | 51 | Done | 2026.02.15 | Done | 84 | Done | 2026.02.09 | Done | 117 | Done | 2026.01.19 | Done
|  | 19 |  |  | 52 |  |  |  | 85 |  |  |  | 118
|  | 20 |  |  | 53 |  |  |  | 86 | Done | 2026.01.17 | Done | 119
|  | 21 |  |  | 54 | Done | 2026.01.31 | Done | 87 | Done | 2026.01.25 | Done | 120 | Done | 2026.02.23 | Done
|  | 22 |  |  | 55 | Done | 2026.03.14 |  | 88 | Done | 2026.02.20 | Done | 121
|  | 23 | 2026.03.05 | Done | 56 | Done | 2026.02.04 | Done | 89 | Done | 2026.01.27 | Done | 122
|  | 24 |  |  | 57 |  |  |  | 90 |  |  |  | 123
|  | 25 | 2026.03.11 | Done | 58 | DOne | 2026.03.13 |  | 91 |  |  |  | 124
|  | 26 |  |  | 59 | Done | 2026.02.28 | Done | 92 |  |  |  | 125 | Done | 2026.02.25 | Done
|  | 27 |  |  | 60 |  |  |  | 93 | Done | 2026.02.26 | Done | 126 | Done | 2026.03.03 | Done
|  | 28 |  |  | 61 |  |  |  | 94 |  |  |  | 127 | Done | 2026.01.28 | Done
|  | 29 |  |  | 62 | Done | 2026.02.12 | Done | 95 |  |  |  | 128
|  | 30 | 2026.03.08 | Done | 63 |  |  |  | 96 | Done | 2026.02.10 | Done | 129 | Done | 2026.02.16 | Done
|  | 31 | 2026.02.18 | Done | 64 | Done | 2026.02.11 | Done | 97 |  |  |  | 130 | Done | 2026.01.16 | Done
|  | 32 | 2026.03.12 | Done | 65 | Done | 2026.02.21 | Done | 98 |  |  |  | 131 | Done | 2026.01.20 | Done
|  | 33 | 2026.03.07 | Done | 66 | Done | 2026.01.21 | Done | 99 | Done | 2026.01.23 | Done | 132 | Done | 2026.01.13 | Done
ARCS ROBOT BOX-HY | Cleaning brushes + Cleaning module + Follow Checklist | 2026-03-01 |  | 2026-03-02 |  | 2026-03-03 |  | 2026-03-04 |  | 2026-03-05 |  | 2026-03-06 |  | 2026-03-07 |  | 2026-03-08 |  | 2026-03-09 |  | 2026-03-10 |  | 2026-03-11 |  | 2026-03-12 |  | 2026-03-13 |  | 2026-03-14 |  | 2026-03-15 |  | 2026-03-16 |  | 2026-03-17 |  | 2026-03-18 |  | 2026-03-19 |  | 2026-03-20 |  | 2026-03-21 |  | 2026-03-22 |  | 2026-03-23 |  | 2026-03-24 |  | 2026-03-25 |  | 2026-03-26 |  | 2026-03-27 |  | 2026-03-28 |  | 2026-03-29 |  | 2026-03-30 |  | 2026-03-31
|  | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist | Robots | Checklist
|  | 20 | Done | 20 | Done | 23 | Done | 20 | Done | 20 | Done | 23 | Done | 20 | Done | 20 | Done | 25 | Done | 20 | Done | 22 | Done | 20 | Done
HVAC Maintenance-Q | Cleaning of Filter+ Wire tightness checking+Gas checking+Follow checklist | PACU 1A |  | PACU 1B |  | PACU 2A |  | PACU 2B |  | PACU 3A |  | PACU 3B |  | PACU 4A |  | PACU 4B
|  | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist | Performed | Checklist

## SCB
Total |  |  | 56
Rectified |  |  | 62
Pending |  |  | -6
S. No | Date | BLOCK | SCB No | SCB Aalrm | Action Taken | Rectification Date | Status | Remarks
1 | 2025-11-14 | 19 | 9 | Outaged | SCB ON | 2025-11-17 | Done
2 | 2025-11-14 | 38 | 28 | Outaged | Fuse buckets replaced | 2025-12-03 | Done
3 | 2025-11-14 | 46 | 17 | Outaged | SCB ON | 2025-11-14 | Done
4 | 2025-11-15 | 65 | 15 | Outaged | SCB ON | 2025-11-18 | Done
5 | 2025-11-15 | 76 | 16 | Outaged | SCB ON | 2025-11-18 | Done
6 | 2025-11-15 | 89 | 32 | Outaged | SCB ON | 2025-11-18 | Done
7 | 2025-11-15 | 91 | 32 | Outaged | SCB ON | 2025-11-18 | Done
8 | 2025-11-15 | 91 | 34 | Outaged | SCB ON | 2025-11-19 | Done
9 | 2025-11-15 | 92 | 29 | Outaged | SCB ON | 2025-11-19 | Done | on Site ok but Communication issue
10 | 2025-11-15 | 99 | 3 | Outaged | SCB ON | 2025-11-19 | Done
11 | 2025-11-15 | 99 | 18 | Outaged | SCB ON | 2025-11-20 | Done
12 | 2025-11-15 | 102 | 36 | Outaged | SCB ON | 2025-11-20 | Done
13 | 2025-11-15 | 104 | 32 | Outaged | SCB ON | 2025-11-20 | Done
14 | 2025-11-15 | 129 | 23 | Outaged | SCB ON | 2025-11-20 | Done
15 | 2025-11-18 | 8 | 17 | Outaged | LV Cable termination replaced | 2025-12-02 | Done
16 | 2025-11-18 | 33 | 26 | Outaged | Rectified | 2025-11-29 | Done
17 | 2025-11-18 | 65 | 15 | Outaged | SCB ON | 2025-11-21 | Done
18 | 2025-11-18 | 100 | 15 | Outaged | SCB ON | 2025-11-21 | Done
19 | 2025-11-18 | 100 | 18 | Outaged | SCB ON | 2025-11-21 | Done
20 | 2025-11-18 | 102 | 36 | Outaged | SCB ON | 2025-11-21 | Done
21 | 2025-11-18 | 125 | 17 | Outaged | Fuse buckets replaced | 2025-12-02 | Done
22 | 2025-11-18 | 130 | 10 | Outaged | SCB ON | 2025-11-22 | Done
23 | 2025-11-20 | 130 | 14 | Outaged | SCB ON | 2025-11-22 | Done
24 | 2025-11-21 | 99 | 18 | Outaged | SCB ON | 2025-11-23 | Done
25 | 2025-11-22 | 101 | 15 | Outaged | SCB ON | 2025-11-23 | Done
26 | 2025-11-23 | 11 | 11 | Outaged | SCB ON | 2025-11-23 | Done
27 | 2025-11-23 | 100 | 18 | Outaged | SCB ON | 2025-11-24 | Done
28 | 2025-11-23 | 101 | 25 | Outaged | SCB ON | 2025-11-24 | Done
29 | 2025-11-26 | 47 | 24 | Outaged | SCB ON | 2025-11-26 | Done
30 | 2025-11-26 | 84 | 32 | Outaged | SCB ON | 2025-11-26 | Done
31 | 2025-11-27 | 11 | 22 | Outaged | SCB ON | 2025-11-27 | Done
32 | 2025-11-30 | 76 | 16 | Outaged | LV Cable termination replaced | 2025-12-01 | Done
33 | 2025-11-30 | 52 | 26 | Outaged | SCB ON | 2025-11-30 | Done
34 | 2025-11-30 | 55 | 16 | Outaged | SCB ON | 2025-11-30 | Done
35 | 2025-12-03 | 93 | 13 | Outaged | Rectified | 2025-12-03 | Done
36 | 2025-12-07 | 82 | 12 | Outaged | On Field found OK | 2025-12-07 | Done
37 | 2025-12-07 | 92 | 29 | Outaged | On Field found OK | 2025-12-07 | Done
38 | 2025-12-08 | 125 | 17 | Outaged | Rectified | 2025-12-10 | Done
39 | 2025-12-09 | 11 | 33 | Outaged | On Field found OK | 2025-12-09 | Done
40 | 2025-12-09 | 17 | 27 | Outaged | On Field found OK | 2025-12-09 | Done
41 | 2025-12-11 | 92 | 29 | Outaged | On Field found OK | 2025-12-11 | Done
42 | 2025-12-12 | 92 | 33 | Outaged | On Field found OK | 2025-12-12 | Done
43 | 2026-01-07 | 53 | 33 | Outaged | On Field found OK | 2026-01-07 | Done
44 | 2026-01-07 | 106 | 29 | Outaged | On Field found OK | 2026-01-07 | Done
45 | 2026-01-11 | 29 | 8 | Outaged | On Field found OK | 2026-01-11 | Done
46 | 2026-01-15 | 76 | 16 | SCB Burn | Replaced disconnector switch | 2026-01-16 | Done
47 | 2026-01-19 | 86 | 29 | Outaged | On Field found OK | 2026-01-19 | Done
48 | 2026-01-20 | 117 | 35 | Outaged | On Field found OK | 2026-01-20 | Done
49 | 2026-01-21 | 131 | 24 | Outaged | On Field found OK | 2026-01-21 | Done
50 | 2026-01-28 | 129 | 4 | Outaged | On Field found OK | 2026-01-28 | Done
51 | 2026-02-02 | 36 | 27 | Outaged | On Field found OK | 2026-02-02 | Done
52 | 2026-02-05 | 56 | 14 | Outaged | Turn ON SCB | 2026-02-05 | Done
53 | 2026-02-08 | 121 | 33 | Outaged | On Field found OK | 2026-02-08 | Done
54 | 2026-02-09 | 110 | 5 | SCB Positive cable burn | SCB Lugs changed | 2026-02-10 | Done
55 | 2026-02-14 | 61 | 5 | Outaged | On Field found OK | 2026-02-14 | Done
56 | 2026-03-03 | 76 | 25 | Outaged | On Field found OK | 2026-03-03 | Done
57 | 2026-03-11 | 30 | 17 | Outaged | On Field found OK | 2026-03-09 | Done
58 | 2026-03-12 | 75 | 26 | Outaged | On Field found OK | 2026-03-12 | Done
59 | 2026-03-15 | 55 | 7 | Outaged | On Field found OK | 2026-03-15 | Done
60 | 2026-03-15 | 55 | 10 | Outaged | On Field found OK | 2026-03-15 | Done
61 | 2026-03-15 | 55 | 15 | Outaged | On Field found OK | 2026-03-15 | Done
62 | 2026-03-15 | 75 | 26 | Outaged | On Field found OK | 2026-03-15 | Done

## Trackers
Total |  |  |  |  | 1353
Done |  |  |  |  | 1345
Pending |  |  |  |  | 8
S. No | Date | BLOCK | TRACKER No | Tracker alarm | Action Taken | Rectification date | Status | Remarks
1 | 2025-11-13 | 4 | 3 | Stop | Reset the tracker | 2025-11-16 | Done
2 | 2025-11-13 | 7 | 140 | Stop | Reset the tracker | 2025-11-16 | Done
3 | 2025-11-13 | 7 | 141 | Stop | Reset the tracker | 2025-11-16 | Done
4 | 2025-11-13 | 20 | 83 | Stop | Reset the tracker | 2025-11-16 | Done
5 | 2025-11-13 | 22 | 64 | Stop | Reset the tracker | 2025-11-16 | Done
6 | 2025-11-13 | 33 | 34 | Stop | Reset the tracker | 2025-11-16 | Done
7 | 2025-11-13 | 38 | 46 | Stop | Reset the tracker | 2025-11-16 | Done
8 | 2025-11-13 | 41 | 89 | Stop | Reset the tracker | 2025-11-16 | Done
9 | 2025-11-13 | 47 | 140 | Stop | Reset the tracker | 2025-11-16 | Done
10 | 2025-11-13 | 47 | 141 | MotorOverCur | Reset the tracker | 2025-11-16 | Done
11 | 2025-11-13 | 47 | 142 | Stop | Reset the tracker | 2025-11-16 | Done
12 | 2025-11-13 | 56 | 61 | Stop | Reset the tracker | 2025-11-16 | Done
13 | 2025-11-13 | 56 | 65 | MotorOverCur | Reset the tracker | 2025-11-16 | Done
14 | 2025-11-13 | 56 | 71 | Emergency Stop | Emergency Released | 2025-11-16 | Done
15 | 2025-11-13 | 56 | 122 | Stop | Reset the tracker | 2025-11-16 | Done
16 | 2025-11-13 | 56 | 140 | Stop | Reset the tracker | 2025-11-16 | Done
17 | 2025-11-13 | 56 | 141 | Stop | Reset the tracker | 2025-11-16 | Done
18 | 2025-11-13 | 56 | 142 | Stop | Reset the tracker | 2025-11-16 | Done
19 | 2025-11-13 | 56 | 143 | Stop | Reset the tracker | 2025-11-16 | Done
20 | 2025-11-13 | 56 | 144 | Stop | Reset the tracker | 2025-11-16 | Done
21 | 2025-11-13 | 56 | 145 | Stop | Reset the tracker | 2025-11-16 | Done
22 | 2025-11-13 | 56 | 146 | Stop | Reset the tracker | 2025-11-16 | Done
23 | 2025-11-13 | 56 | 147 | Stop | Reset the tracker | 2025-11-16 | Done
24 | 2025-11-13 | 56 | 148 | Stop | Reset the tracker | 2025-11-16 | Done
25 | 2025-11-13 | 56 | 149 | Stop | Reset the tracker | 2025-11-16 | Done
26 | 2025-11-13 | 56 | 150 | Stop | Reset the tracker | 2025-11-16 | Done
27 | 2025-11-13 | 56 | 151 | Stop | Reset the tracker | 2025-11-16 | Done
28 | 2025-11-13 | 75 | 72 | Stop | Reset the tracker | 2025-11-16 | Done
29 | 2025-11-13 | 83 | 99 | Stop | Reset the tracker | 2025-11-16 | Done
30 | 2025-11-13 | 85 | 139 | Stop | Reset the tracker | 2025-11-16 | Done
31 | 2025-11-13 | 98 | 69 | Stop | Reset the tracker | 2025-11-16 | Done
32 | 2025-11-13 | 104 | 32 | Stop | Reset the tracker | 2025-11-16 | Done
33 | 2025-11-13 | 113 | 136 | Stop | Reset the tracker | 2025-11-16 | Done
34 | 2025-11-13 | 118 | 89 | Stop | Reset the tracker | 2025-11-16 | Done
35 | 2025-11-13 | 119 | 126 | Stop | Reset the tracker | 2025-11-16 | Done
36 | 2025-11-14 | 4 | 26 | MotorOverCur | Reset the tracker | 2025-11-16 | Done
37 | 2025-11-14 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-11-16 | Done
38 | 2025-11-14 | 8 | 8 | MotorOverCur | Reset the tracker | 2025-11-16 | Done
39 | 2025-11-14 | 13 | 46 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
40 | 2025-11-14 | 13 | 60 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
41 | 2025-11-14 | 37 | 88 | Emergency Stop | Emergency Released | 2025-11-17 | Done
42 | 2025-11-14 | 37 | 92 | Emergency Stop | Emergency Released | 2025-11-17 | Done
43 | 2025-11-14 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
44 | 2025-11-14 | 38 | 46 | Emergency Stop | Emergency Released | 2025-11-17 | Done
45 | 2025-11-14 | 42 | 38 | Emergency Stop | Emergency Released | 2025-11-17 | Done
46 | 2025-11-14 | 42 | 97 | Emergency Stop | Emergency Released | 2025-11-17 | Done
47 | 2025-11-14 | 44 | 12 | Emergency Stop | Emergency Released | 2025-11-17 | Done
48 | 2025-11-14 | 47 | 14 | Emergency Stop | Emergency Released | 2025-11-17 | Done
49 | 2025-11-14 | 48 | 141 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
50 | 2025-11-14 | 48 | 22 | Emergency Stop | Emergency Released | 2025-11-17 | Done
51 | 2025-11-14 | 53 | 41 | Emergency Stop | Emergency Released | 2025-11-17 | Done
52 | 2025-11-14 | 56 | 61 | Emergency Stop | Emergency Released | 2025-11-17 | Done
53 | 2025-11-14 | 56 | 73 | Emergency Stop | Emergency Released | 2025-11-17 | Done
54 | 2025-11-14 | 56 | 131 | Emergency Stop | Emergency Released | 2025-11-17 | Done
55 | 2025-11-14 | 59 | 109 | Emergency Stop | Emergency Released | 2025-11-17 | Done
56 | 2025-11-14 | 60 | 41 | Emergency Stop | Emergency Released | 2025-11-17 | Done
57 | 2025-11-14 | 79 | 61 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
58 | 2025-11-14 | 80 | 52 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
59 | 2025-11-14 | 86 | 104 | Emergency Stop | Emergency Released | 2025-11-17 | Done
60 | 2025-11-14 | 94 | 129 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
61 | 2025-11-14 | 107 | 116 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
62 | 2025-11-14 | 117 | 121 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
63 | 2025-11-14 | 129 | 48 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
64 | 2025-11-14 | 129 | 28 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
65 | 2025-11-14 | 131 | 109 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
66 | 2025-11-15 | 4 | 26 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
67 | 2025-11-15 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
68 | 2025-11-15 | 20 | 102 | Emergency Stop | Emergency Released | 2025-11-17 | Done
69 | 2025-11-15 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
70 | 2025-11-15 | 38 | 46 | Emergency Stop | Emergency Released | 2025-11-17 | Done
71 | 2025-11-15 | 42 | 38 | Emergency Stop | Emergency Released | 2025-11-17 | Done
72 | 2025-11-15 | 42 | 97 | Emergency Stop | Emergency Released | 2025-11-17 | Done
73 | 2025-11-15 | 43 | 78 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
74 | 2025-11-15 | 44 | 12 | Emergency Stop | Emergency Released | 2025-11-17 | Done
75 | 2025-11-15 | 47 | 14 | Emergency Stop | Emergency Released | 2025-11-17 | Done
76 | 2025-11-15 | 47 | 141 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
77 | 2025-11-15 | 48 | 22 | Emergency Stop | Emergency Released | 2025-11-17 | Done
78 | 2025-11-15 | 53 | 41 | Emergency Stop | Emergency Released | 2025-11-17 | Done
79 | 2025-11-15 | 56 | 61 | Emergency Stop | Emergency Released | 2025-11-17 | Done
80 | 2025-11-15 | 56 | 73 | Emergency Stop | Emergency Released | 2025-11-17 | Done
81 | 2025-11-15 | 56 | 131 | Emergency Stop | Emergency Released | 2025-11-17 | Done
82 | 2025-11-15 | 58 | 60 | Emergency Stop | Emergency Released | 2025-11-17 | Done
83 | 2025-11-15 | 59 | 109 | Emergency Stop | Emergency Released | 2025-11-17 | Done
84 | 2025-11-15 | 60 | 41 | MotorReversal | Reset the tracker | 2025-11-17 | Done
85 | 2025-11-15 | 79 | 61 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
86 | 2025-11-15 | 80 | 52 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
87 | 2025-11-15 | 86 | 104 | Emergency Stop | Emergency Released | 2025-11-17 | Done
88 | 2025-11-15 | 94 | 129 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
89 | 2025-11-15 | 104 | 116 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
90 | 2025-11-15 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
91 | 2025-11-15 | 131 | 109 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
92 | 2025-11-16 | 3 | 115 | MotorOverCur | Replaced | 2025-12-08 | Done | transmission shaft damage
93 | 2025-11-16 | 4 | 26 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
94 | 2025-11-16 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
95 | 2025-11-16 | 8 | 8 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
96 | 2025-11-16 | 16 | 112 | Emergency Stop | Emergency Released | 2025-11-17 | Done
97 | 2025-11-16 | 20 | 26 | Emergency Stop | Emergency Released | 2025-11-17 | Done
98 | 2025-11-16 | 20 | 82 | Emergency Stop | Emergency Released | 2025-11-17 | Done
99 | 2025-11-16 | 20 | 102 | Emergency Stop | Emergency Released | 2025-11-17 | Done
100 | 2025-11-16 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
101 | 2025-11-16 | 38 | 46 | Emergency Stop | Emergency Released | 2025-11-17 | Done
102 | 2025-11-16 | 42 | 38 | Emergency Stop | Emergency Released | 2025-11-17 | Done
103 | 2025-11-16 | 42 | 97 | Emergency Stop | Emergency Released | 2025-11-17 | Done
104 | 2025-11-16 | 43 | 78 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
105 | 2025-11-16 | 47 | 14 | Emergency Stop | Emergency Released | 2025-11-17 | Done
106 | 2025-11-16 | 47 | 141 | MotorOverCur | Reset the tracker | 2025-11-17 | Done
107 | 2025-11-16 | 48 | 22 | Emergency Stop | Emergency Released | 2025-11-17 | Done
108 | 2025-11-16 | 53 | 41 | Emergency Stop | Emergency Released | 2025-11-17 | Done
109 | 2025-11-17 | 56 | 61 | Emergency Stop | Emergency Released | 2025-11-17 | Done
110 | 2025-11-17 | 56 | 65 | Emergency Stop | Emergency Released | 2025-11-17 | Done
111 | 2025-11-17 | 56 | 71 | Emergency Stop | Emergency Released | 2025-11-17 | Done
112 | 2025-11-17 | 56 | 73 | Emergency Stop | Emergency Released | 2025-11-17 | Done
113 | 2025-11-17 | 56 | 131 | Emergency Stop | Emergency Released | 2025-11-17 | Done
114 | 2025-11-17 | 59 | 109 | Emergency Stop | Emergency Released | 2025-11-18 | Done
115 | 2025-11-17 | 60 | 41 | MotorReversal | Reset the tracker | 2025-11-18 | Done
116 | 2025-11-18 | 18 | 66 | No Communication | Reset the tracker | 2025-11-18 | Done
117 | 2025-11-18 | 33 | 17 | No Communication | Set to Auto mode | 2025-11-18 | Done
118 | 2025-11-18 | 38 | 7 | MotorOverCur | T connector replaced | 2025-11-29 | Done | Dc power issue
119 | 2025-11-18 | 38 | 46 | Stop | Reset the tracker | 2025-11-18 | Done
120 | 2025-11-18 | 39 | 60 | Stop | Set to Auto mode | 2025-11-18 | Done
121 | 2025-11-18 | 47 | 14 | Stop | Reset the tracker | 2025-11-18 | Done
122 | 2025-11-18 | 47 | 140 | Stop | Set to Auto mode | 2025-11-18 | Done
123 | 2025-11-18 | 47 | 141 | MotorOverCur | Set to Auto mode | 2025-11-18 | Done
124 | 2025-11-18 | 47 | 142 | Stop | Set to Auto mode | 2025-11-18 | Done
125 | 2025-11-18 | 56 | 140 | Stop | Set to Auto mode | 2025-11-18 | Done
126 | 2025-11-18 | 56 | 141 | Stop | Set to Auto mode | 2025-11-18 | Done
127 | 2025-11-18 | 56 | 142 | Stop | Set to Auto mode | 2025-11-18 | Done
128 | 2025-11-18 | 56 | 143 | Stop | Set to Auto mode | 2025-11-18 | Done
129 | 2025-11-18 | 56 | 144 | Stop | Set to Auto mode | 2025-11-18 | Done
130 | 2025-11-18 | 56 | 145 | Stop | Set to Auto mode | 2025-11-18 | Done
131 | 2025-11-18 | 56 | 146 | Stop | Set to Auto mode | 2025-11-18 | Done
132 | 2025-11-18 | 56 | 147 | Stop | Set to Auto mode | 2025-11-18 | Done
133 | 2025-11-18 | 56 | 148 | Stop | Set to Auto mode | 2025-11-18 | Done
134 | 2025-11-18 | 56 | 149 | Stop | Set to Auto mode | 2025-11-18 | Done
135 | 2025-11-18 | 56 | 150 | Stop | Emergency released | 2025-11-18 | Done
136 | 2025-11-18 | 56 | 151 | Stop | Rectified | 2025-11-26 | Done | Dc power issue
137 | 2025-11-18 | 59 | 73 | Stop | Set to Auto mode | 2025-11-18 | Done
138 | 2025-11-18 | 83 | 99 | Stop | Set to Auto mode | 2025-11-18 | Done
139 | 2025-11-18 | 98 | 69 | Stop | Set to Auto mode | 2025-11-18 | Done
140 | 2025-11-18 | 103 | 111 | Stop | Set to Auto mode | 2025-11-18 | Done
141 | 2025-11-18 | 103 | 113 | Stop | Reset the tracker | 2025-11-18 | Done
142 | 2025-11-18 | 104 | 32 | Stop | Rectified | 2025-11-26 | Done | DC power issue
143 | 2025-11-18 | 113 | 136 | Stop | Set to Auto mode | 2025-11-18 | Done
144 | 2025-11-18 | 118 | 89 | Stop | Set to Auto mode | 2025-11-18 | Done
145 | 2025-11-18 | 119 | 126 | Stop | Set to Auto mode | 2025-11-18 | Done
146 | 2025-11-20 | 3 | 115 | EmergencyStop | Emergency Released | 2025-11-20 | Done
147 | 2025-11-20 | 8 | 51 | EmergencyStop | Emergency Released | 2025-11-20 | Done
148 | 2025-11-20 | 8 | 57 | EmergencyStop | Emergency Released | 2025-11-20 | Done
149 | 2025-11-20 | 15 | 12 | EmergencyStop | Emergency Released | 2025-11-20 | Done
150 | 2025-11-20 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
151 | 2025-11-20 | 42 | 38 | EmergencyStop | Emergency Released | 2025-11-20 | Done
152 | 2025-11-20 | 42 | 97 | EmergencyStop | Emergency Released | 2025-11-20 | Done
153 | 2025-11-20 | 43 | 16 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
154 | 2025-11-20 | 43 | 78 | EmergencyStop | Emergency Released | 2025-11-20 | Done
155 | 2025-11-20 | 48 | 12 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
156 | 2025-11-20 | 48 | 22 | EmergencyStop | Emergency Released | 2025-11-20 | Done
157 | 2025-11-20 | 53 | 41 | EmergencyStop | Emergency Released | 2025-11-20 | Done
158 | 2025-11-20 | 56 | 71 | EmergencyStop | Emergency Released | 2025-11-20 | Done
159 | 2025-11-20 | 58 | 26 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
160 | 2025-11-20 | 66 | 52 | EmergencyStop | Emergency Released | 2025-11-20 | Done
161 | 2025-11-20 | 80 | 52 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
162 | 2025-11-20 | 94 | 129 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
163 | 2025-11-20 | 104 | 116 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
164 | 2025-11-20 | 117 | 121 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
165 | 2025-11-20 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-11-20 | Done
166 | 2025-11-21 | 7 | 141 | no communication | Reset the Tracker | 2025-11-21 | Done
167 | 2025-11-21 | 33 | 17 | no communication | reset the tracker | 2025-11-21 | Done
168 | 2025-11-21 | 39 | 60 | no communication | Y Connector replaced | 2025-12-07 | Done | DC Power Issue
169 | 2025-11-21 | 81 | 132 | no communication | reset the tracker | 2025-11-21 | Done
170 | 2025-11-21 | 83 | 99 | no communication | Reset the tracker | 2025-12-01 | Done | DC Power Issue
171 | 2025-11-21 | 86 | 101 | no communication | reset the tracker | 2025-11-21 | Done
172 | 2025-11-21 | 107 | 130 | no communication | reset the tracker | 2025-11-21 | Done
173 | 2025-11-21 | 107 | 131 | no communication | reset the tracker | 2025-11-21 | Done
174 | 2025-11-21 | 107 | 132 | no communication | reset the tracker | 2025-11-21 | Done
175 | 2025-11-21 | 107 | 134 | no communication | reset the tracker | 2025-11-21 | Done
176 | 2025-11-21 | 118 | 89 | no communication | Resolved | 2025-12-02 | Done | DC Power Issue
177 | 2025-11-22 | 3 | 36 | EmergencyStop | emergency released | 2025-11-22 | Done
178 | 2025-11-22 | 3 | 114 | EmergencyStop | Transmission shaft replaced | 2025-11-26 | Done | transmission shaft damage
179 | 2025-11-22 | 8 | 8 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
180 | 2025-11-22 | 9 | 99 | EmergencyStop | emergency released | 2025-11-22 | Done
181 | 2025-11-22 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
182 | 2025-11-22 | 42 | 38 | EmergencyStop | Replaced | 2025-12-07 | Done | transmission shaft damage
183 | 2025-11-22 | 42 | 97 | EmergencyStop | emergency released | 2025-11-22 | Done
184 | 2025-11-22 | 43 | 16 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
185 | 2025-11-22 | 43 | 78 | EmergencyStop | Replaced | 2025-12-09 | Done | transmission shaft damage
186 | 2025-11-22 | 47 | 14 | No Communication | Reset the tracker | 2025-11-22 | Done
187 | 2025-11-22 | 47 | 140 | No Communication | Issue from SCADA. Resolved | 2025-11-22 | Done
188 | 2025-11-22 | 47 | 141 | No Communication | Issue from SCADA. Resolved | 2025-11-22 | Done
189 | 2025-11-22 | 47 | 142 | No Communication | Issue from SCADA. Resolved | 2025-11-22 | Done
190 | 2025-11-22 | 48 | 12 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
191 | 2025-11-22 | 53 | 122 | EmergencyStop | emergency released | 2025-11-22 | Done
192 | 2025-11-22 | 56 | 71 | EmergencyStop | Transmission shaft replaced | 2025-11-26 | Done | transmission shaft damage
193 | 2025-11-22 | 58 | 43 | EmergencyStop | Replaced | 2025-12-02 | Done | transmission shaft damage
194 | 2025-11-22 | 66 | 52 | EmergencyStop | Rectified | 2025-11-26 | Done | DC power issue
195 | 2025-11-22 | 68 | 113 | EmergencyStop | emergency released | 2025-11-22 | Done
196 | 2025-11-22 | 80 | 52 | MotorOverCur | reset the tracker | 2025-11-22 | Done
197 | 2025-11-22 | 86 | 101 | No Communication | Reset the tracker | 2025-11-22 | Done
198 | 2025-11-22 | 94 | 129 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
199 | 2025-11-22 | 104 | 32 | No Communication | Issue from SCADA. Resolved | 2025-11-22 | Done
200 | 2025-11-22 | 104 | 116 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
201 | 2025-11-22 | 107 | 96 | No Communication | Reset the tracker | 2025-11-22 | Done
202 | 2025-11-22 | 107 | 110 | No Communication | Reset the tracker | 2025-11-22 | Done
203 | 2025-11-22 | 107 | 112 | No Communication | Reset the tracker | 2025-11-22 | Done
204 | 2025-11-22 | 107 | 113 | No Communication | Reset the tracker | 2025-11-22 | Done
205 | 2025-11-22 | 107 | 122 | No Communication | Reset the tracker | 2025-11-22 | Done
206 | 2025-11-22 | 107 | 124 | No Communication | Reset the tracker | 2025-11-22 | Done
207 | 2025-11-22 | 107 | 126 | No Communication | Reset the tracker | 2025-11-22 | Done
208 | 2025-11-22 | 107 | 131 | No Communication | Reset the tracker | 2025-11-22 | Done
209 | 2025-11-22 | 107 | 136 | No Communication | Reset the tracker | 2025-11-22 | Done
210 | 2025-11-22 | 107 | 139 | No Communication | Reset the tracker | 2025-11-22 | Done
211 | 2025-11-22 | 117 | 121 | MotorOverCur | Reset the tracker | 2025-11-22 | Done
212 | 2025-11-22 | 121 | 48 | EmergencyStop | Reset the tracker | 2025-11-22 | Done
213 | 2025-11-23 | 2 | 68 | EmergencyStop | emergency released | 2025-11-23 | Done
214 | 2025-11-23 | 2 | 71 | EmergencyStop | emergency released | 2025-11-23 | Done
215 | 2025-11-23 | 8 | 8 | EmergencyStop | emergency released | 2025-11-23 | Done
216 | 2025-11-23 | 9 | 111 | no communication | Replaced | 2025-12-07 | Done | Gaskit missing
217 | 2025-11-23 | 22 | 44 | MotorOverCur | Reset the tracker | 2025-11-23 | Done
218 | 2025-11-23 | 38 | 7 | EmergencyStop | emergency released | 2025-11-23 | Done
219 | 2025-11-23 | 38 | 46 | no communication | Replaced | 2025-12-07 | Done | Gaskit missing
220 | 2025-11-23 | 43 | 16 | EmergencyStop | emergency released | 2025-11-23 | Done
221 | 2025-11-23 | 48 | 12 | EmergencyStop | Replaced | 2025-12-02 | Done | Transmission shaft damage
222 | 2025-11-23 | 64 | 20 | EmergencyStop | emergency released | 2025-11-23 | Done
223 | 2025-11-23 | 68 | 113 | MotorOverCur | Reset the tracker | 2025-11-23 | Done
224 | 2025-11-23 | 80 | 54 | no communication | Reset the tracker | 2025-11-23 | Done
225 | 2025-11-23 | 94 | 129 | no communication | Reset the tracker | 2025-11-23 | Done
226 | 2025-11-23 | 107 | 97 | no communication | Reset the tracker | 2025-11-23 | Done
227 | 2025-11-23 | 107 | 116 | MotorOverCur | Reset the tracker | 2025-11-23 | Done
228 | 2025-11-23 | 115 | 15 | MotorOverCur | Replaced | 2025-12-04 | Done | Transmission shaft damage
229 | 2025-11-23 | 117 | 121 | no communication | Rectified | 2025-11-26 | Done | Transmission shaft damage
230 | 2025-11-23 | 121 | 48 | stop | Reset the tracker | 2025-11-23 | Done
231 | 2025-11-25 | 34 | 127 | AngleNoChg | Reset the tracker | 2025-11-25 | Done
232 | 2025-11-25 | 37 | 124 | AngleNoChg | Reset the tracker | 2025-11-25 | Done
233 | 2025-11-25 | 38 | 7 | MotorOverCur | Reset the tracker | 2025-11-25 | Done
234 | 2025-11-25 | 47 | 141 | AngleNoChg | Reset the tracker | 2025-11-25 | Done
235 | 2025-11-25 | 64 | 20 | AngleNoChg | Reset the tracker | 2025-11-25 | Done
236 | 2025-11-25 | 68 | 113 | EmergencyStop | Emergency Released | 2025-11-25 | Done
237 | 2025-11-25 | 80 | 95 | AngleNoCom | reset the tracker | 2025-11-25 | Done
238 | 2025-11-25 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-11-25 | Done
239 | 2025-11-25 | 127 | 76 | AngleNoChg | Reset the tracker | 2025-11-25 | Done
240 | 2025-11-26 | 4 | 26 | BatSOCLow | Reset the tracker | 2025-11-26 | Done
241 | 2025-11-26 | 23 | 22 | BatSOCLow | Reset the tracker | 2025-11-26 | Done
242 | 2025-11-26 | 34 | 127 | Angle no change | Gaskit Installed | 2025-12-02 | Done | Gaskit missing
243 | 2025-11-26 | 38 | 6 | no communication | Reset the tracker | 2025-11-26 | Done
244 | 2025-11-26 | 47 | 141 | EmergencyStop | Replaced | 2025-12-07 | Done | Transmission shaft damage
245 | 2025-11-26 | 54 | 55 | EmergencyStop | Emergency released | 2025-11-26 | Done
246 | 2025-11-26 | 58 | 31 | EmergencyStop | emergency released | 2025-12-01 | Done | Transmission shaft damage
247 | 2025-11-26 | 61 | 134 | EmergencyStop | Replaced | 2025-12-02 | Done | Gaskit missing
248 | 2025-11-26 | 64 | 20 | EmergencyStop | Replaced | 2025-12-07 | Done | Gaskit missing
249 | 2025-11-26 | 68 | 113 | EmergencyStop | emergency released | 2025-12-01 | Done | Alignment issue
250 | 2025-11-26 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-11-26 | Done
251 | 2025-11-26 | 94 | 129 | MotorOverCur | Reset the tracker | 2025-11-26 | Done
252 | 2025-11-26 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-11-26 | Done
253 | 2025-11-26 | 115 | 32 | EmergencyStop | Emergency released | 2025-11-26 | Done
254 | 2025-11-26 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-11-26 | Done
255 | 2025-11-26 | 131 | 109 | MotorOverCur | Reset the tracker | 2025-11-26 | Done
256 | 2025-11-27 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-11-27 | Done
257 | 2025-11-27 | 37 | 124 | AngleNoChg | Reset the tracker | 2025-11-27 | Done
258 | 2025-11-27 | 42 | 125 | AngleNoChg | Reset the tracker | 2025-11-27 | Done
259 | 2025-11-27 | 120 | 133 | EmergencyStop | Reset the tracker | 2025-11-30 | Done
260 | 2025-11-28 | 4 | 61 | Stop | Reset the tracker | 2025-11-28 | Done
261 | 2025-11-28 | 37 | 124 | AngleNoChg | Cable connected | 2025-11-28 | Done
262 | 2025-11-28 | 42 | 125 | AngleNoChg | Cable connected | 2025-11-28 | Done
263 | 2025-11-28 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-11-28 | Done
264 | 2025-11-28 | 121 | 148 | MotorOverCur | Reset the tracker | 2025-11-28 | Done
265 | 2025-11-28 | 131 | 109 | BatSOCLow | Reset the tracker | 2025-11-28 | Done
266 | 2025-11-30 | 4 | 26 | BatSOCLow | Reset the tracker | 2025-11-30 | Done
267 | 2025-11-30 | 4 | 61 | Battery Error | Reset the tracker | 2025-11-30 | Done
268 | 2025-11-30 | 16 | 131 | Emergency Stop | Replaced | 2025-12-06 | Done | Transmission shaft damage
269 | 2025-11-30 | 30 | 2 | no communication | Reset the tracker | 2025-11-30 | Done
270 | 2025-11-30 | 33 | 71 | MotorOverCur | Rectified | 2025-12-02 | Done | Transmission shaft damage
271 | 2025-11-30 | 37 | 71 | Angle no change | Reset the tracker | 2025-11-30 | Done
272 | 2025-11-30 | 42 | 97 | emergency stop | Replaced | 2025-12-02 | Done | Transmission shaft damage
273 | 2025-11-30 | 42 | 125 | anglenochange | Replaced | 2025-12-02 | Done | Module Damage
274 | 2025-11-30 | 56 | 8 | No Communication | Reset the tracker | 2025-11-30 | Done
275 | 2025-11-30 | 56 | 63 | emergency stop | emergency released | 2025-11-30 | Done
276 | 2025-11-30 | 56 | 75 | emergency stop | emergency released | 2025-11-30 | Done
277 | 2025-11-30 | 56 | 140 | emergency stop | emergency released | 2025-11-30 | Done
278 | 2025-11-30 | 56 | 147 | emergency stop | emergency released | 2025-11-30 | Done
279 | 2025-11-30 | 57 | 29 | MotoroverCurrent | Reset the tracker | 2025-11-30 | Done
280 | 2025-11-30 | 58 | 119 | MotorReversal | Reset the tracker | 2025-11-30 | Done
281 | 2025-11-30 | 79 | 62 | MotoroverCurrent | Reset the tracker | 2025-11-30 | Done
282 | 2025-11-30 | 80 | 95 | anglenochange | Cable connected | 2025-11-30 | Done
283 | 2025-11-30 | 82 | 30 | BatSOCLow | reset the tracker | 2025-11-30 | Done
284 | 2025-11-30 | 98 | 10 | STOP | reset the tracker | 2025-11-30 | Done
285 | 2025-11-30 | 113 | 136 | No Communication | reset the tracker | 2025-11-30 | Done
286 | 2025-11-30 | 119 | 67 | MotoroverCurrent | Replaced | 2025-12-03 | Done | Gaskit missing
287 | 2025-11-30 | 119 | 102 | MotoroverCurrent | Bolt Installed | 2025-12-03 | Done | Bolt missing
288 | 2025-11-30 | 121 | 48 | MotoroverCurrent | reset the tracker | 2025-11-30 | Done
289 | 2025-11-30 | 122 | 125 | emergency stop | Replaced | 2025-12-07 | Done | transmission shaft damage
290 | 2025-11-30 | 125 | 124 | STOP | reset the tracker | 2025-11-30 | Done
291 | 2025-11-30 | 125 | 126 | STOP | reset the tracker | 2025-11-30 | Done
292 | 2025-11-30 | 125 | 128 | STOP | reset the tracker | 2025-11-30 | Done
293 | 2025-11-30 | 125 | 130 | STOP | reset the tracker | 2025-11-30 | Done
294 | 2025-11-30 | 125 | 132 | STOP | reset the tracker | 2025-11-30 | Done
295 | 2025-12-01 | 56 | 79 | EmergencyStop | Emergency released | 2025-12-02 | Done | transmission shaft damage
296 | 2025-12-01 | 57 | 29 | AngleNoChg | reset the tracker | 2025-12-01 | Done
297 | 2025-12-01 | 2 | 11 | no communication | burent firmwear with stlink | 2025-12-01 | Done
298 | 2025-12-01 | 4 | 61 | BatSOCLow | Reset the tracker | 2025-12-01 | Done
299 | 2025-12-01 | 8 | 129 | stop | set to clean mode | 2025-12-01 | Done
300 | 2025-12-01 | 8 | 131 | stop | set to cleane mode | 2025-12-01 | Done
301 | 2025-12-01 | 8 | 133 | stop | set to cleane mode | 2025-12-01 | Done
302 | 2025-12-01 | 13 | 53 | EmergencyStop | Reset the tracker | 2025-12-01 | Done
303 | 2025-12-01 | 14 | 55 | EmergencyStop | Emergency release | 2025-12-01 | Done
304 | 2025-12-01 | 14 | 55 | EmergencyStop | Emergency release | 2025-12-01 | Done
305 | 2025-12-01 | 30 | 2 | No Communication | Reset channel ID | 2025-12-01 | Done
306 | 2025-12-01 | 58 | 33 | No Communication | Replaced | 2025-12-02 | Done | transmission shaft damage
307 | 2025-12-01 | 68 | 137 | No Communication | Reset the tracker | 2025-12-01 | Done
308 | 2025-12-01 | 70 | 61 | no communication | reset the tracker | 2025-12-01 | Done
309 | 2025-12-01 | 75 | 72 | stop | reset the tracker | 2025-12-01 | Done
310 | 2025-12-01 | 82 | 30 | BatSOCLow | reset the tracker | 2025-12-01 | Done
311 | 2025-12-01 | 83 | 143 | MotorOverCur | reset the tracker | 2025-12-01 | Done
312 | 2025-12-01 | 87 | 69 | no communication | reset the tracker | 2025-12-01 | Done
313 | 2025-12-01 | 95 | 3 | no communication | reset the tracker | 2025-12-01 | Done
314 | 2025-12-01 | 95 | 135 | no communication | reset the tracker | 2025-12-01 | Done
315 | 2025-12-01 | 121 | 48 | motorovercur | reset the tracker | 2025-12-01 | Done
316 | 2025-12-02 | 16 | 88 | AngleNoChg | Done | 2025-12-07 | Done | Alignment issue
317 | 2025-12-02 | 19 | 20 | MotorOverCur | Reset the tracker | 2025-12-02 | Done
318 | 2025-12-02 | 58 | 119 | MotorReversal | Reset the tracker | 2025-12-02 | Done
319 | 2025-12-02 | 68 | 137 | no communication | Burnt firmware with st link | 2025-12-02 | Done
320 | 2025-12-02 | 83 | 143 | MotorOverCur | Reset the tracker | 2025-12-02 | Done
321 | 2025-12-02 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-02 | Done
322 | 2025-12-02 | 130 | 45 | MotorOverCur | Replaced | 2025-12-06 | Done | transmission shaft damage
323 | 2025-12-03 | 2 | 11 | no communication | Reset the tracker | 2025-12-03 | Done
324 | 2025-12-03 | 8 | 133 | lowpower | Reset the tracker | 2025-12-03 | Done
325 | 2025-12-03 | 16 | 112 | STOP | Done | 2025-12-07 | Done | Alignment issue
326 | 2025-12-03 | 22 | 44 | nocommunication | Reset the tracker | 2025-12-03 | Done
327 | 2025-12-03 | 23 | 30 | no-communication | Reset the tracker | 2025-12-03 | Done
328 | 2025-12-03 | 28 | 64 | nocommunication | Reset the tracker | 2025-12-03 | Done
329 | 2025-12-03 | 30 | 118 | nocommunication | Reset the tracker | 2025-12-03 | Done
330 | 2025-12-03 | 33 | 71 | STOPMODE | set to auto mode | 2025-12-03 | Done
331 | 2025-12-03 | 37 | 124 | anglenochange | cable connected | 2025-12-03 | Done
332 | 2025-12-03 | 46 | 28 | nocommunication | Reset the tracker | 2025-12-03 | Done
333 | 2025-12-03 | 55 | 97 | nocommunication | Reset the tracker | 2025-12-03 | Done
334 | 2025-12-03 | 58 | 119 | motorreversal | Reset the tracker | 2025-12-03 | Done
335 | 2025-12-03 | 63 | 87 | anglenochange | cable connected | 2025-12-03 | Done
336 | 2025-12-03 | 70 | 49 | nocommunication | Reset the tracker | 2025-12-03 | Done
337 | 2025-12-03 | 70 | 61 | nocommunication | Reset the tracker | 2025-12-03 | Done
338 | 2025-12-03 | 79 | 120 | nocommunication | Reset the tracker | 2025-12-03 | Done
339 | 2025-12-03 | 80 | 95 | anglenochange | cable connected | 2025-12-03 | Done
340 | 2025-12-03 | 83 | 143 | motorovercurrent | Reset the tracker | 2025-12-03 | Done
341 | 2025-12-03 | 91 | 36 | batterylow | reset the tracker | 2025-12-03 | Done
342 | 2025-12-03 | 98 | 10 | lowbattery | reset the tracker | 2025-12-03 | Done
343 | 2025-12-03 | 112 | 89 | nocommuniucation | Reset the tracker | 2025-12-03 | Done
344 | 2025-12-03 | 121 | 48 | motoovercurrent | Reset the tracker | 2025-12-03 | Done
345 | 2025-12-03 | 121 | 64 | motorreversal | Reset the tracker | 2025-12-03 | Done
346 | 2025-12-03 | 127 | 108 | nocommunication | Reset the tracker | 2025-12-03 | Done
347 | 2025-12-03 | 58 | 26 | Emergency Stop | Done | 2025-12-11 | Done | Alignment issue
348 | 2025-12-04 | 4 | 26 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
349 | 2025-12-04 | 4 | 61 | MotorOverCur | Reset the tacker | 2025-12-04 | Done
350 | 2025-12-04 | 8 | 113 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
351 | 2025-12-04 | 25 | 63 | BatError | Reset the tacker | 2025-12-04 | Done
352 | 2025-12-04 | 37 | 71 | AngleNoChg | Reset the tacker | 2025-12-04 | Done
353 | 2025-12-04 | 42 | 125 | Stop | Set to auto | 2025-12-04 | Done
354 | 2025-12-04 | 46 | 98 | no communication | Reset the tacker | 2025-12-04 | Done
355 | 2025-12-04 | 54 | 104 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
356 | 2025-12-04 | 62 | 80 | no communication | Reset the tacker | 2025-12-04 | Done
357 | 2025-12-04 | 70 | 49 | no communication | Reset the tacker | 2025-12-04 | Done
358 | 2025-12-04 | 70 | 61 | no communication | Reset the tacker | 2025-12-04 | Done
359 | 2025-12-04 | 80 | 95 | AngleNoChg | cable connected | 2025-12-04 | Done
360 | 2025-12-04 | 82 | 30 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
361 | 2025-12-04 | 83 | 143 | MotorOverCur | Reset the tacker | 2025-12-04 | Done
362 | 2025-12-04 | 86 | 23 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
363 | 2025-12-04 | 86 | 32 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
364 | 2025-12-04 | 86 | 61 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
365 | 2025-12-04 | 86 | 84 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
366 | 2025-12-04 | 86 | 108 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
367 | 2025-12-04 | 91 | 36 | Stop | Set to auto mode | 2025-12-04 | Done
368 | 2025-12-04 | 94 | 19 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
369 | 2025-12-04 | 95 | 66 | BatSOCLow | Reset the tacker | 2025-12-04 | Done
370 | 2025-12-04 | 101 | 4 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
371 | 2025-12-04 | 101 | 5 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
372 | 2025-12-04 | 101 | 33 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
373 | 2025-12-04 | 101 | 43 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
374 | 2025-12-04 | 101 | 45 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
375 | 2025-12-04 | 101 | 60 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
376 | 2025-12-04 | 101 | 82 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
377 | 2025-12-04 | 101 | 88 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
378 | 2025-12-04 | 101 | 95 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
379 | 2025-12-04 | 101 | 99 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
380 | 2025-12-04 | 101 | 101 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
381 | 2025-12-04 | 112 | 89 | no communication | Reset the tacker | 2025-12-04 | Done
382 | 2025-12-04 | 115 | 116 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
383 | 2025-12-04 | 118 | 89 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
384 | 2025-12-04 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-04 | Done
385 | 2025-12-04 | 125 | 108 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
386 | 2025-12-04 | 125 | 116 | AngleNoChg | Cable connected | 2025-12-04 | Done
387 | 2025-12-04 | 125 | 118 | EmergencyStop | Reset the tracker | 2025-12-04 | Done
388 | 2025-12-04 | 125 | 122 | AngleNoChg | Cable connected | 2025-12-04 | Done
389 | 2025-12-04 | 129 | 112 | AngleNoChg | cable connected | 2025-12-04 | Done
390 | 2025-12-04 | 132 | 53 | BatSOCLow | Reset the tracker | 2025-12-04 | Done
391 | 2025-12-06 | 4 | 26 | BatSOCLow | Reset the tracker | 2025-12-06 | Done
392 | 2025-12-06 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-12-06 | Done
393 | 2025-12-06 | 28 | 64 | no communication | Reset the tracker | 2025-12-06 | Done
394 | 2025-12-06 | 37 | 124 | no communication | Reset the tracker | 2025-12-06 | Done
395 | 2025-12-06 | 54 | 104 | no communication | Reset the tracker | 2025-12-06 | Done
396 | 2025-12-06 | 58 | 48 | AngleNoChg | Reset the tracker | 2025-12-06 | Done
397 | 2025-12-06 | 58 | 119 | MotorReversal | Reset the tracker | 2025-12-06 | Done
398 | 2025-12-06 | 60 | 91 | no communication | Reset the tracker | 2025-12-06 | Done
399 | 2025-12-06 | 62 | 80 | no communication | Reset the tracker | 2025-12-06 | Done
400 | 2025-12-06 | 80 | 26 | no communication | Reset the tracker | 2025-12-06 | Done
401 | 2025-12-06 | 81 | 125 | no communication | Reset the tracker | 2025-12-06 | Done
402 | 2025-12-06 | 82 | 30 | BatSOCLow | Reset the tracker | 2025-12-06 | Done
403 | 2025-12-06 | 83 | 143 | MotorOverCur | Reset the tracker | 2025-12-06 | Done
404 | 2025-12-06 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-06 | Done
405 | 2025-12-06 | 112 | 85 | EmergencyStop | Emergency released | 2025-12-06 | Done
406 | 2025-12-06 | 114 | 113 | stop | Reset the tracker | 2025-12-06 | Done
407 | 2025-12-06 | 115 | 116 | EmergencyStop | Emergency released | 2025-12-06 | Done
408 | 2025-12-06 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-06 | Done
409 | 2025-12-06 | 127 | 127 | BatSOCLow | Reset the tracker | 2025-12-06 | Done
410 | 2025-12-06 | 131 | 68 | no communication | Reset the tracker | 2025-12-06 | Done
411 | 2025-12-06 | 132 | 53 | BatSOCLow | Reset the tracker | 2025-12-06 | Done
412 | 2025-12-07 | 13 | 104 | MotorOverCur | Replaced | 2025-12-13 | Done | Transmission shaft damage
413 | 2025-12-07 | 58 | 48 | EmergencyStop | Replaced | 2025-12-11 | Done | Transmission shaft damage
414 | 2025-12-07 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-08 | Done
415 | 2025-12-07 | 121 | 98 | EmergencyStop | Replaced | 2025-12-08 | Done | Gaskit missing
416 | 2025-12-07 | 1 | 41 | BatSOCLow | Reset the Tracker | 2025-12-07 | Done
417 | 2025-12-07 | 4 | 26 | BatSOCLow | Reset the Tracker | 2025-12-07 | Done
418 | 2025-12-07 | 4 | 61 | MotorOverCur | Reset the Tracker | 2025-12-07 | Done
419 | 2025-12-07 | 28 | 64 | BatError | Reset the tracker | 2025-12-07 | Done
420 | 2025-12-07 | 29 | 33 | MotorOverCur | Reset the tracker | 2025-12-07 | Done
421 | 2025-12-07 | 58 | 119 | Stop | Found Ok on field | 2025-12-07 | Done
422 | 2025-12-07 | 58 | 146 | BatSOCLow | Reset the tracker | 2025-12-07 | Done
423 | 2025-12-07 | 62 | 80 | no communication | Reset the tracker | 2025-12-07 | Done
424 | 2025-12-07 | 69 | 34 | no communication | Reset the tracker | 2025-12-07 | Done
425 | 2025-12-07 | 80 | 26 | no communication | Reset the Tracker | 2025-12-07 | Done
426 | 2025-12-07 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-07 | Done
427 | 2025-12-07 | 98 | 10 | BatSOCLow | Reset the tracker | 2025-12-07 | Done
428 | 2025-12-07 | 112 | 56 | MotorReversal | Reset the tracker | 2025-12-07 | Done
429 | 2025-12-07 | 112 | 60 | MotorReversal | Reset the tracker | 2025-12-07 | Done
430 | 2025-12-07 | 112 | 62 | MotorReversal | Reset the tracker | 2025-12-07 | Done
431 | 2025-12-07 | 112 | 66 | MotorReversal | Reset the tracker | 2025-12-07 | Done
432 | 2025-12-07 | 112 | 96 | EmergencyStop | Emergency Released | 2025-12-07 | Done
433 | 2025-12-07 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-07 | Done
434 | 2025-12-07 | 130 | 95 | BatSOCLow | Reset the tracker | 2025-12-07 | Done
435 | 2025-12-07 | 131 | 53 | no communication | Tracker found ok | 2025-12-07 | Done
436 | 2025-12-08 | 33 | 83 | AngleNoChg | Replaced | 2025-12-11 | Done | Transmission shaft damage
437 | 2025-12-08 | 48 | 136 | AngleNoChg | Replaced | 2025-12-14 | Done | Transmission shaft damage
438 | 2025-12-08 | 1 | 41 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
439 | 2025-12-08 | 2 | 1 | MotorReversal | Reset the tracker | 2025-12-08 | Done
440 | 2025-12-08 | 4 | 26 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
441 | 2025-12-08 | 4 | 61 | AngleNoChg | Cable connected | 2025-12-08 | Done
442 | 2025-12-08 | 9 | 111 | EmergencyStop | Emergency released | 2025-12-08 | Done
443 | 2025-12-08 | 18 | 73 | EmergencyStop | Emergency released | 2025-12-08 | Done
444 | 2025-12-08 | 23 | 123 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
445 | 2025-12-08 | 28 | 103 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
446 | 2025-12-08 | 29 | 75 | AngleNoChg | Cable connected | 2025-12-08 | Done
447 | 2025-12-08 | 29 | 80 | EmergencyStop | Emergency released | 2025-12-08 | Done
448 | 2025-12-08 | 56 | 11 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
449 | 2025-12-08 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
450 | 2025-12-08 | 56 | 108 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
451 | 2025-12-08 | 58 | 146 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
452 | 2025-12-08 | 64 | 10 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
453 | 2025-12-08 | 69 | 34 | no communication | Reset the tracker | 2025-12-08 | Done
454 | 2025-12-08 | 79 | 120 | no communication | Reset the tracker | 2025-12-08 | Done
455 | 2025-12-08 | 98 | 10 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
456 | 2025-12-08 | 122 | 125 | EmergencyStop | Emergency released | 2025-12-08 | Done
457 | 2025-12-08 | 130 | 95 | BatSOCLow | Reset the tracker | 2025-12-08 | Done
458 | 2025-12-09 | 56 | 55 | MotorOverCur | Replaced | 2025-12-11 | Done | Transmission shaft damage
459 | 2025-12-09 | 58 | 76 | MotorOverCur | Replaced | 2025-12-11 | Done | Alignment issue
460 | 2025-12-09 | 71 | 86 | MotorOverCur | Replaced | 2025-12-17 | Done | Transmission shaft damage
461 | 2025-12-09 | 121 | 98 | EmergencyStop | Rectified | 2025-12-11 | Done | Gaskit missing
462 | 2025-12-09 | 4 | 61 | AngleNoChg | Cable connected | 2025-12-09 | Done
463 | 2025-12-09 | 18 | 103 | no communication | Reset the tracker | 2025-12-09 | Done
464 | 2025-12-09 | 23 | 30 | no communication | Reset the tracker | 2025-12-09 | Done
465 | 2025-12-09 | 23 | 54 | no communication | Reset the tracker | 2025-12-09 | Done
466 | 2025-12-09 | 23 | 123 | BatSOCLow | Reset the tracker | 2025-12-09 | Done
467 | 2025-12-09 | 28 | 64 | no communication | Reset the tracker | 2025-12-09 | Done
468 | 2025-12-09 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-09 | Done
469 | 2025-12-09 | 56 | 108 | BatSOCLow | Reset the tracker | 2025-12-09 | Done
470 | 2025-12-09 | 79 | 120 | no communication | Reset the tracker | 2025-12-09 | Done
471 | 2025-12-09 | 80 | 26 | no communication | Reset the tracker | 2025-12-09 | Done
472 | 2025-12-09 | 83 | 143 | MotorOverCur | Reset the tracker | 2025-12-09 | Done
473 | 2025-12-09 | 99 | 46 | MotorReversal | Reset the tracker | 2025-12-09 | Done
474 | 2025-12-09 | 99 | 48 | MotorReversal | Reset the tracker | 2025-12-09 | Done
475 | 2025-12-09 | 99 | 50 | MotorReversal | Reset the tracker | 2025-12-09 | Done
476 | 2025-12-09 | 99 | 52 | MotorReversal | Reset the tracker | 2025-12-09 | Done
477 | 2025-12-09 | 99 | 53 | MotorReversal | Reset the tracker | 2025-12-09 | Done
478 | 2025-12-09 | 99 | 54 | MotorReversal | Reset the tracker | 2025-12-09 | Done
479 | 2025-12-09 | 99 | 56 | MotorReversal | Reset the tracker | 2025-12-09 | Done
480 | 2025-12-09 | 99 | 58 | MotorReversal | Reset the tracker | 2025-12-09 | Done
481 | 2025-12-09 | 99 | 60 | MotorReversal | Reset the tracker | 2025-12-09 | Done
482 | 2025-12-09 | 99 | 62 | MotorReversal | Reset the tracker | 2025-12-09 | Done
483 | 2025-12-09 | 99 | 64 | MotorReversal | Reset the tracker | 2025-12-09 | Done
484 | 2025-12-09 | 99 | 66 | MotorReversal | Reset the tracker | 2025-12-09 | Done
485 | 2025-12-09 | 99 | 68 | MotorReversal | Reset the tracker | 2025-12-09 | Done
486 | 2025-12-09 | 99 | 70 | MotorReversal | Reset the tracker | 2025-12-09 | Done
487 | 2025-12-09 | 106 | 51 | no communication | no communication | 2025-12-09 | Done
488 | 2025-12-09 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-09 | Done
489 | 2025-12-10 | 4 | 61 | AngleNoChg | Reset the tracker | 2025-12-10 | Done
490 | 2025-12-10 | 22 | 107 | no communication | Reset the tracker | 2025-12-10 | Done
491 | 2025-12-10 | 23 | 123 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
492 | 2025-12-10 | 26 | 93 | no communication | Reset the tracker | 2025-12-10 | Done
493 | 2025-12-10 | 26 | 94 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
494 | 2025-12-10 | 28 | 64 | no communication | Reset the tracker | 2025-12-10 | Done
495 | 2025-12-10 | 29 | 33 | MotorOverCur | Reset the tracker | 2025-12-10 | Done
496 | 2025-12-10 | 35 | 63 | BatError | Reset the tracker | 2025-12-10 | Done
497 | 2025-12-10 | 35 | 64 | BatError | Reset the tracker | 2025-12-10 | Done
498 | 2025-12-10 | 37 | 124 | AngleNoChg | Reset the tracker | 2025-12-10 | Done
499 | 2025-12-10 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
500 | 2025-12-10 | 79 | 63 | MotorOverCur | Reset the tracker | 2025-12-10 | Done
501 | 2025-12-10 | 79 | 120 | no communication | Reset the tracker | 2025-12-10 | Done
502 | 2025-12-10 | 80 | 46 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
503 | 2025-12-10 | 80 | 95 | AngleNoCom | Reset the tracker | 2025-12-10 | Done
504 | 2025-12-10 | 101 | 63 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
505 | 2025-12-10 | 102 | 129 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
506 | 2025-12-10 | 112 | 62 | no communication | Reset the tracker | 2025-12-10 | Done
507 | 2025-12-10 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
508 | 2025-12-10 | 115 | 116 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
509 | 2025-12-10 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-10 | Done
510 | 2025-12-10 | 125 | 130 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
511 | 2025-12-10 | 125 | 132 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
512 | 2025-12-10 | 126 | 39 | no communication | Reset the tracker | 2025-12-10 | Done
513 | 2025-12-10 | 126 | 40 | BatSOCLow | Reset the tracker | 2025-12-10 | Done
514 | 2025-12-10 | 130 | 98 | EmergencyStop | Reset the tracker | 2025-12-10 | Done
515 | 2025-12-11 | 126 | 39 | no communication | Resolved | 2025-12-14 | Done | DC Power Issue
516 | 2025-12-11 | 5 | 5 | no communication | Reset the tracker | 2025-12-11 | Done
517 | 2025-12-11 | 17 | 60 | MotorOverCur | Reset the tracker | 2025-12-11 | Done
518 | 2025-12-11 | 19 | 20 | MotorReversal | Reset the tracker | 2025-12-11 | Done
519 | 2025-12-11 | 26 | 93 | no communication | Reset the tracker | 2025-12-11 | Done
520 | 2025-12-11 | 26 | 94 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
521 | 2025-12-11 | 28 | 64 | no communication | Reset the tracker | 2025-12-11 | Done
522 | 2025-12-11 | 29 | 33 | MotorOverCur | Reset the tracker | 2025-12-11 | Done
523 | 2025-12-11 | 35 | 63 | no communication | Reset the tracker | 2025-12-11 | Done
524 | 2025-12-11 | 35 | 64 | no communication | Reset the tracker | 2025-12-11 | Done
525 | 2025-12-11 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
526 | 2025-12-11 | 61 | 63 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
527 | 2025-12-11 | 63 | 135 | no communication | Reset the tracker | 2025-12-11 | Done
528 | 2025-12-11 | 79 | 63 | MotorOverCur | Reset the tracker | 2025-12-11 | Done
529 | 2025-12-11 | 91 | 9 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
530 | 2025-12-11 | 91 | 72 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
531 | 2025-12-11 | 94 | 67 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
532 | 2025-12-11 | 94 | 137 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
533 | 2025-12-11 | 94 | 139 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
534 | 2025-12-11 | 99 | 32 | MotorReversal | Reset the tracker | 2025-12-11 | Done
535 | 2025-12-11 | 99 | 34 | MotorReversal | Reset the tracker | 2025-12-11 | Done
536 | 2025-12-11 | 99 | 36 | MotorReversal | Reset the tracker | 2025-12-11 | Done
537 | 2025-12-11 | 99 | 38 | MotorReversal | Reset the tracker | 2025-12-11 | Done
538 | 2025-12-11 | 99 | 40 | MotorReversal | Reset the tracker | 2025-12-11 | Done
539 | 2025-12-11 | 99 | 42 | MotorReversal | Reset the tracker | 2025-12-11 | Done
540 | 2025-12-11 | 99 | 44 | MotorReversal | Reset the tracker | 2025-12-11 | Done
541 | 2025-12-11 | 99 | 48 | MotorReversal | Reset the tracker | 2025-12-11 | Done
542 | 2025-12-11 | 99 | 61 | AngleNoChg | Reset the tracker | 2025-12-11 | Done
543 | 2025-12-11 | 99 | 64 | MotorReversal | Reset the tracker | 2025-12-11 | Done
544 | 2025-12-11 | 99 | 83 | MotorReversal | Reset the tracker | 2025-12-11 | Done
545 | 2025-12-11 | 99 | 86 | MotorReversal | Reset the tracker | 2025-12-11 | Done
546 | 2025-12-11 | 102 | 129 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
547 | 2025-12-11 | 108 | 18 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
548 | 2025-12-11 | 108 | 20 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
549 | 2025-12-11 | 112 | 130 | MotorReversal | Reset the tracker | 2025-12-11 | Done
550 | 2025-12-11 | 112 | 132 | MotorReversal | Reset the tracker | 2025-12-11 | Done
551 | 2025-12-11 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
552 | 2025-12-11 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-11 | Done
553 | 2025-12-11 | 121 | 48 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
554 | 2025-12-11 | 122 | 125 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
555 | 2025-12-11 | 125 | 132 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
556 | 2025-12-11 | 126 | 40 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
557 | 2025-12-11 | 129 | 112 | AngleNoChg | Reset the tracker | 2025-12-11 | Done
558 | 2025-12-11 | 130 | 98 | BatSOCLow | Reset the tracker | 2025-12-11 | Done
559 | 2025-12-12 | 26 | 93 | no communication | Resolved | 2025-12-14 | Done | DC Power Issue
560 | 2025-12-12 | 66 | 20 | AngleNoChg | Replaced | 2025-12-14 | Done | Motor Drive fail / Transmission shaft damage
561 | 2025-12-12 | 102 | 129 | BatSOCLow | Rectified | 2025-12-13 | Done | DC Power Issue
562 | 2025-12-12 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-12-12 | Done
563 | 2025-12-12 | 5 | 5 | no communication | Tracker found ok on field | 2025-12-12 | Done
564 | 2025-12-12 | 21 | 126 | no communication | Reset the tracker | 2025-12-12 | Done
565 | 2025-12-12 | 26 | 94 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
566 | 2025-12-12 | 38 | 87 | no communication | Reset the tracker | 2025-12-12 | Done
567 | 2025-12-12 | 43 | 18 | AngleNoChg | Reset the tracker | 2025-12-12 | Done
568 | 2025-12-12 | 59 | 68 | no communication | Reset the tracker | 2025-12-12 | Done
569 | 2025-12-12 | 61 | 63 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
570 | 2025-12-12 | 66 | 25 | no communication | Reset the tracker | 2025-12-12 | Done
571 | 2025-12-12 | 79 | 63 | MotorOverCur | Reset the tracker | 2025-12-12 | Done
572 | 2025-12-12 | 80 | 46 | no communication | Reset the tracker | 2025-12-12 | Done
573 | 2025-12-12 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-12 | Done
574 | 2025-12-12 | 83 | 143 | MotorOverCur | Reset the tracker | 2025-12-12 | Done
575 | 2025-12-12 | 87 | 94 | MotorReversal | Reset the tracker | 2025-12-12 | Done
576 | 2025-12-12 | 88 | 69 | no communication | Reset the tracker | 2025-12-12 | Done
577 | 2025-12-12 | 94 | 67 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
578 | 2025-12-12 | 94 | 137 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
579 | 2025-12-12 | 94 | 139 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
580 | 2025-12-12 | 99 | 14 | MotorReversal | Reset the tracker | 2025-12-12 | Done
581 | 2025-12-12 | 99 | 20 | MotorReversal | Reset the tracker | 2025-12-12 | Done
582 | 2025-12-12 | 99 | 22 | MotorReversal | Reset the tracker | 2025-12-12 | Done
583 | 2025-12-12 | 99 | 30 | MotorReversal | Reset the tracker | 2025-12-12 | Done
584 | 2025-12-12 | 99 | 32 | MotorReversal | Reset the tracker | 2025-12-12 | Done
585 | 2025-12-12 | 99 | 61 | AngleNoChg | Reset the tracker | 2025-12-12 | Done
586 | 2025-12-12 | 99 | 64 | no communication | Reset the tracker | 2025-12-12 | Done
587 | 2025-12-12 | 108 | 18 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
588 | 2025-12-12 | 108 | 20 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
589 | 2025-12-12 | 112 | 136 | no communication | Reset the tracker | 2025-12-12 | Done
590 | 2025-12-12 | 121 | 48 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
591 | 2025-12-12 | 122 | 125 | BatSOCLow | Reset the tracker | 2025-12-12 | Done
592 | 2025-12-12 | 126 | 40 | BatError | Reset the tracker | 2025-12-12 | Done
593 | 2025-12-12 | 130 | 98 | no communication | Reset the tracker | 2025-12-12 | Done
594 | 2025-12-13 | 58 | 26 | EmergencyStop | Rectified | 2025-12-14 | Done | Alignment issue
595 | 2025-12-13 | 80 | 46 | BatSOCLow | Rectified | 2025-12-14 | Done | DC Power issue
596 | 2025-12-13 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-12-13 | Done
597 | 2025-12-13 | 26 | 94 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
598 | 2025-12-13 | 29 | 33 | MotorOverCur | Reset the tracker | 2025-12-13 | Done
599 | 2025-12-13 | 43 | 18 | AngleNoChg | Reset the tracker | 2025-12-13 | Done
600 | 2025-12-13 | 59 | 71 | no communication | Reset the tracker | 2025-12-13 | Done
601 | 2025-12-13 | 61 | 61 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
602 | 2025-12-13 | 64 | 20 | AngleNoChg | Reset the tracker | 2025-12-13 | Done
603 | 2025-12-13 | 68 | 137 | no communication | Reset the tracker | 2025-12-13 | Done
604 | 2025-12-13 | 79 | 63 | MotorOverCur | Reset the tracker | 2025-12-13 | Done
605 | 2025-12-13 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-13 | Done
606 | 2025-12-13 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
607 | 2025-12-13 | 94 | 67 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
608 | 2025-12-13 | 94 | 137 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
609 | 2025-12-13 | 94 | 139 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
610 | 2025-12-13 | 99 | 2 | MotorReversal | Reset the tracker | 2025-12-13 | Done
611 | 2025-12-13 | 99 | 4 | MotorReversal | Reset the tracker | 2025-12-13 | Done
612 | 2025-12-13 | 99 | 6 | MotorReversal | Reset the tracker | 2025-12-13 | Done
613 | 2025-12-13 | 99 | 8 | MotorReversal | Reset the tracker | 2025-12-13 | Done
614 | 2025-12-13 | 99 | 10 | MotorReversal | Reset the tracker | 2025-12-13 | Done
615 | 2025-12-13 | 108 | 18 | BatError | Reset the tracker | 2025-12-13 | Done
616 | 2025-12-13 | 108 | 20 | BatError | Reset the tracker | 2025-12-13 | Done
617 | 2025-12-13 | 111 | 95 | BatError | Reset the tracker | 2025-12-13 | Done
618 | 2025-12-13 | 112 | 130 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
619 | 2025-12-13 | 112 | 132 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
620 | 2025-12-13 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
621 | 2025-12-13 | 121 | 48 | MotorOverCur | Reset the tracker | 2025-12-13 | Done
622 | 2025-12-13 | 121 | 50 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
623 | 2025-12-13 | 121 | 125 | BatSOCLow | Reset the tracker | 2025-12-13 | Done
624 | 2025-12-14 | 22 | 98 | BatSOCLow | Resolved | 2025-12-17 | Done | DC Power Issue
625 | 2025-12-14 | 36 | 39 | EmergencyStop | Replaced | 2025-12-15 | Done | Gaskit missing
626 | 2025-12-14 | 58 | 76 | EmergencyStop | Rectified | 2026-01-01 | Done | Slew driver failure
627 | 2025-12-14 | 7 | 87 | AngleNoChg | Reset the tracker | 2025-12-14 | Done
628 | 2025-12-14 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-14 | Done
629 | 2025-12-14 | 87 | 71 | no communication | Reset the tracker | 2025-12-14 | Done
630 | 2025-12-14 | 91 | 36 | no communication | Reset the tracker | 2025-12-14 | Done
631 | 2025-12-14 | 99 | 9 | AngleNoChg | Reset the tracker | 2025-12-14 | Done
632 | 2025-12-14 | 99 | 115 | no communication | Reset the tracker | 2025-12-14 | Done
633 | 2025-12-14 | 99 | 125 | MotorReversal | Reset the tracker | 2025-12-14 | Done
634 | 2025-12-14 | 126 | 9 | no communication | Reset the tracker | 2025-12-14 | Done
635 | 2025-12-15 | 58 | 26 | EmergencyStop | Rectified | 2025-12-19 | Done | Alignment issue
636 | 2025-12-15 | 58 | 87 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
637 | 2025-12-15 | 64 | 20 | MotorOverCur | Rectified | 2025-12-18 | Done | Alignment issue
638 | 2025-12-15 | 126 | 39 | no communication | Resolved | 2025-12-21 | Done | Dc power issue
639 | 2025-12-15 | 13 | 104 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
640 | 2025-12-15 | 28 | 103 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
641 | 2025-12-15 | 33 | 71 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
642 | 2025-12-15 | 42 | 31 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
643 | 2025-12-15 | 54 | 104 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
644 | 2025-12-15 | 66 | 132 | no communication | Reset the tracker | 2025-12-15 | Done
645 | 2025-12-15 | 70 | 63 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
646 | 2025-12-15 | 79 | 84 | no communication | Reset the tracker | 2025-12-15 | Done
647 | 2025-12-15 | 80 | 46 | no communication | Reset the tracker | 2025-12-15 | Done
648 | 2025-12-15 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-15 | Done
649 | 2025-12-15 | 87 | 28 | AngleNoChg | Reset the tracker | 2025-12-15 | Done
650 | 2025-12-15 | 90 | 99 | no communication | Reset the tracker | 2025-12-15 | Done
651 | 2025-12-15 | 99 | 1 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
652 | 2025-12-15 | 99 | 5 | BatSOCLow | Reset the tracker | 2025-12-15 | Done
653 | 2025-12-16 | 26 | 93 | no communication | Rectified | 2025-12-26 | Done | DC Power issue
654 | 2025-12-16 | 129 | 76 | MotorOverCur | Replaced | 2025-12-17 | Done | Transmission shaft damage
655 | 2025-12-16 | 10 | 69 | EmergencyStop | Reset the tracketr | 2025-12-16 | Done
656 | 2025-12-16 | 28 | 103 | no communication | Reset the tracker | 2025-12-16 | Done
657 | 2025-12-16 | 37 | 124 | MotorOverCur | Reset the tracker | 2025-12-16 | Done
658 | 2025-12-16 | 42 | 31 | no communication | Reset the tracker | 2025-12-16 | Done
659 | 2025-12-16 | 56 | 49 | no communication | Reset the tracker | 2025-12-16 | Done
660 | 2025-12-16 | 70 | 63 | no communication | Reset the tracker | 2025-12-16 | Done
661 | 2025-12-16 | 74 | 52 | no communication | Reset the tracker | 2025-12-16 | Done
662 | 2025-12-16 | 79 | 84 | no communication | Reset the tracker | 2025-12-16 | Done
663 | 2025-12-16 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-16 | Done
664 | 2025-12-16 | 87 | 18 | AngleNoChg | Reset the tracker | 2025-12-16 | Done
665 | 2025-12-16 | 87 | 118 | AngleNoChg | Reset the tracker | 2025-12-16 | Done
666 | 2025-12-16 | 99 | 107 | no communication | Reset the tracker | 2025-12-16 | Done
667 | 2025-12-16 | 99 | 136 | no communication | Reset the tracker | 2025-12-16 | Done
668 | 2025-12-16 | 101 | 105 | no communication | Reset the tracker | 2025-12-16 | Done
669 | 2025-12-16 | 128 | 111 | no communication | Reset the tracker | 2025-12-16 | Done
670 | 2025-12-16 | 74 | 25 | no communication | Reset the tracker | 2025-12-16 | Done
671 | 2025-12-17 | 94 | 107 | MotorOverCur | Replaced | 2025-12-19 | Done | Transmission shaft damage
672 | 2025-12-17 | 7 | 65 | EmergencyStop | Reset the tracker | 2025-12-17 | Done
673 | 2025-12-17 | 56 | 11 | BatSOCLow | Reset the tracker | 2025-12-17 | Done
674 | 2025-12-17 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-17 | Done
675 | 2025-12-17 | 74 | 42 | MotorReversal | Reset the tracker | 2025-12-17 | Done
676 | 2025-12-17 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-17 | Done
677 | 2025-12-17 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-17 | Done
678 | 2025-12-17 | 95 | 3 | no communication | Reset the tracker | 2025-12-17 | Done
679 | 2025-12-17 | 109 | 12 | no communication | Reset the tracker | 2025-12-17 | Done
680 | 2025-12-17 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-17 | Done
681 | 2025-12-18 | 19 | 20 | MotorOverCur | Reset the tracker | 2025-12-18 | Done
682 | 2025-12-18 | 71 | 86 | EmergencyStop | Emergency released | 2025-12-18 | Done
683 | 2025-12-18 | 74 | 42 | MotorReversal | Reset the tracker | 2025-12-18 | Done
684 | 2025-12-18 | 80 | 95 | AngleNoChg | Reset the tracker | 2025-12-18 | Done
685 | 2025-12-18 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-18 | Done
686 | 2025-12-18 | 94 | 139 | no communication | Reset the tracker | 2025-12-18 | Done
687 | 2025-12-18 | 95 | 3 | no communication | Reset the tracker | 2025-12-18 | Done
688 | 2025-12-18 | 95 | 66 | no communication | Reset the tracker | 2025-12-18 | Done
689 | 2025-12-18 | 101 | 42 | no communication | Reset the tracker | 2025-12-18 | Done
690 | 2025-12-18 | 101 | 73 | BatSOCLow | Reset the tracker | 2025-12-18 | Done
691 | 2025-12-18 | 109 | 12 | no communication | Reset the tracker | 2025-12-18 | Done
692 | 2025-12-18 | 109 | 21 | no communication | Reset the tracker | 2025-12-18 | Done
693 | 2025-12-18 | 114 | 113 | BatSOCLow | Reset the tracker | 2025-12-18 | Done
694 | 2025-12-18 | 119 | 35 | no communication | Reset the tracker | 2025-12-18 | Done
695 | 2025-12-18 | 131 | 68 | no communication | Reset the tracker | 2025-12-18 | Done
696 | 2025-12-19 | 4 | 26 | BatSOCLow | Reset the tracker | 2025-12-19 | Done
697 | 2025-12-19 | 19 | 20 | MotorOverCur | Reset the tracker | 2025-12-19 | Done
698 | 2025-12-19 | 36 | 61 | MotorReversal | Reset the tracker | 2025-12-19 | Done
699 | 2025-12-19 | 36 | 67 | MotorReversal | Reset the tracker | 2025-12-19 | Done
700 | 2025-12-19 | 36 | 69 | MotorReversal | Reset the tracker | 2025-12-19 | Done
701 | 2025-12-19 | 37 | 124 | AngleNoChg | Reset the tracker | 2025-12-19 | Done
702 | 2025-12-19 | 43 | 18 | MotorOverCur | Reset the tracker | 2025-12-19 | Done
703 | 2025-12-19 | 71 | 98 | MotorOverCur | Reset the tracker | 2025-12-19 | Done
704 | 2025-12-19 | 80 | 40 | no communication | Reset the tracker | 2025-12-19 | Done
705 | 2025-12-19 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-19 | Done
706 | 2025-12-19 | 119 | 35 | no communication | Reset the tracker | 2025-12-19 | Done
707 | 2025-12-21 | 48 | 24 | AngleNoChg | Replaced | 2026-01-02 | Done | Transmission shaft damage
708 | 2025-12-21 | 56 | 125 | EmergencyStop | Replaced | 2025-12-23 | Done | Transmission shaft damage
709 | 2025-12-21 | 59 | 103 | AngleNoChg | Replaced | 2025-12-29 | Done | Transmission shaft damage
710 | 2025-12-21 | 71 | 98 | MotorOverCur | Replaced | 2025-12-22 | Done | Transmission shaft damage
711 | 2025-12-21 | 11 | 102 | BatSOCLow | Reset the tracker | 2025-12-21 | Done
712 | 2025-12-21 | 19 | 63 | EmergencyStop | Emergency released | 2025-12-21 | Done
713 | 2025-12-21 | 25 | 63 | BatError | Reset the tracker | 2025-12-21 | Done
714 | 2025-12-21 | 28 | 7 | MotorOverCur | Reset the tracker | 2025-12-21 | Done
715 | 2025-12-21 | 37 | 124 | AngleNoChg | Reset the tracker | 2025-12-21 | Done
716 | 2025-12-21 | 43 | 18 | MotorOverCur | Reset the tracker | 2025-12-21 | Done
717 | 2025-12-21 | 43 | 74 | no communication | Reset the tracker | 2025-12-21 | Done
718 | 2025-12-21 | 53 | 113 | MotorOverCur | Reset the tracker | 2025-12-21 | Done
719 | 2025-12-21 | 79 | 108 | EmergencyStop | Emergency released | 2025-12-21 | Done
720 | 2025-12-21 | 79 | 120 | BatSOCLow | Reset the tracker | 2025-12-21 | Done
721 | 2025-12-21 | 80 | 40 | no communication | Reset the tracker | 2025-12-21 | Done
722 | 2025-12-21 | 101 | 50 | no communication | Reset the tracker | 2025-12-21 | Done
723 | 2025-12-21 | 106 | 46 | AngleNoChg | Reset the tracker | 2025-12-21 | Done
724 | 2025-12-21 | 109 | 21 | no communication | Reset the tracker | 2025-12-21 | Done
725 | 2025-12-21 | 121 | 98 | BatSOCLow | Reset the tracker | 2025-12-21 | Done
726 | 2025-12-23 | 53 | 113 | MotorOverCur | Replaced | 2026-01-01 | Done | Transmisison shaft damage
727 | 2025-12-23 | 4 | 61 | MotorOverCur | Reset the tracker | 2025-12-23 | Done
728 | 2025-12-23 | 15 | 105 | EmergencyStop | Emergency released | 2025-12-23 | Done
729 | 2025-12-23 | 19 | 20 | MotorOverCur | Reset the tracker | 2025-12-23 | Done
730 | 2025-12-23 | 43 | 74 | no communication | Reset the tracker | 2025-12-23 | Done
731 | 2025-12-24 | 74 | 45 | EmergencyStop | Installed | 2025-12-25 | Done | Gasket missing
732 | 2025-12-24 | 119 | 49 | AngleNoChg | Replaced | 2025-12-25 | Done | Transmission shaft damage
733 | 2025-12-24 | 58 | 26 | EmergencyStop | Rectified | 2025-12-26 | Done | Alignment issue
734 | 2025-12-24 | 4 | 59 | MotorOverCur | Reset the tracker | 2025-12-24 | Done
735 | 2025-12-24 | 16 | 59 | EmergencyStop | Emergency released | 2025-12-24 | Done
736 | 2025-12-24 | 16 | 65 | EmergencyStop | Emergency released | 2025-12-24 | Done
737 | 2025-12-24 | 16 | 78 | EmergencyStop | Emergency released | 2025-12-24 | Done
738 | 2025-12-24 | 16 | 105 | AngleNoChg | Reset the tracker | 2025-12-24 | Done
739 | 2025-12-24 | 80 | 93 | AngleNoChg | Reset the tracker | 2025-12-24 | Done
740 | 2025-12-24 | 91 | 36 | BatSOCLow | Reset the tracker | 2025-12-24 | Done
741 | 2025-12-24 | 93 | 73 | no communication | Reset the tracker | 2025-12-24 | Done
742 | 2025-12-24 | 94 | 19 | no communication | Reset the tracker | 2025-12-24 | Done
743 | 2025-12-25 | 56 | 125 | MotorOverCur | Replaced | 2025-12-30 | Done | Slew drive failure
744 | 2025-12-25 | 82 | 41 | AngleNoChg | Replaced | 2026-01-02 | Done | Transmission shaft damage
745 | 2025-12-25 | 4 | 59 | MotorOverCur | Reset the tracker | 2025-12-25 | Done
746 | 2025-12-25 | 9 | 53 | AngleNoChg | Reset the tracker | 2025-12-25 | Done
747 | 2025-12-25 | 16 | 94 | BatError | Reset the tracker | 2025-12-25 | Done
748 | 2025-12-25 | 41 | 32 | BatSOCLow | Reset the tracker | 2025-12-25 | Done
749 | 2025-12-25 | 75 | 51 | BatSOCLow | Reset the tracker | 2025-12-25 | Done
750 | 2025-12-25 | 80 | 93 | AngleNoChg | Reset the tracker | 2025-12-25 | Done
751 | 2025-12-25 | 95 | 109 | BatError | Reset the tracker | 2025-12-25 | Done
752 | 2025-12-25 | 109 | 55 | AngleNoChg | Reset the tracker | 2025-12-25 | Done
753 | 2025-12-25 | 120 | 128 | no communication | Reset the tracker | 2025-12-25 | Done
754 | 2025-12-25 | 122 | 27 | EmergencyStop | Emergency released | 2025-12-25 | Done
755 | 2025-12-26 | 122 | 120 | AngleNoChg | Rectified | 2025-12-30 | Done | Alignment Issue
756 | 2025-12-26 | 28 | 7 | AngleNoChg | Reset the tracker | 2025-12-26 | Done
757 | 2025-12-26 | 29 | 33 | AngleNoChg | Reset the tracker | 2025-12-26 | Done
758 | 2025-12-26 | 83 | 18 | AngleNoChg | Reset the tracker | 2025-12-26 | Done
759 | 2025-12-26 | 95 | 109 | BatError | Reset the tracker | 2025-12-26 | Done
760 | 2025-12-26 | 109 | 55 | AngleNoChg | Reset the tracker | 2025-12-26 | Done
761 | 2025-12-27 | 58 | 111 | BatError | Rectified | 2025-12-30 | Done | DC Power Issue
762 | 2025-12-27 | 64 | 20 | MotorOverCur | Rectified | 2025-12-29 | Done | Alignment Issue
763 | 2025-12-27 | 56 | 131 | MotorOverCur | Rectified | 2025-12-28 | Done | Alignment Issue
764 | 2025-12-27 | 7 | 74 | BatSOCLow | Reset the tracker | 2025-12-27 | Done
765 | 2025-12-27 | 41 | 33 | Stop | Reset the tracker | 2025-12-27 | Done
766 | 2025-12-27 | 62 | 1 | MotorOverCur | Reset the tracker | 2025-12-27 | Done
767 | 2025-12-27 | 62 | 35 | AngleNoCom | Reset the tracker | 2025-12-27 | Done
768 | 2025-12-27 | 82 | 30 | BatSOCLow | Reset the tracker | 2025-12-27 | Done
769 | 2025-12-27 | 86 | 95 | BatSOCLow | Reset the tracker | 2025-12-27 | Done
770 | 2025-12-27 | 106 | 94 | no communication | Reset the tracker | 2025-12-27 | Done
771 | 2025-12-27 | 120 | 95 | no communication | Reset the tracker | 2025-12-27 | Done
772 | 2025-12-28 | 26 | 93 | no communication | Resolved | 2025-12-31 | Done | Dc power issue
773 | 2025-12-28 | 56 | 132 | EmergencyStop | Rectified | 2025-12-29 | Done | Alignment issue
774 | 2025-12-28 | 78 | 122 | EmergencyStop | Rectified | 2025-12-30 | Done | Dc power issue
775 | 2025-12-28 | 4 | 35 | BatSOCLow | Reset the tracker | 2025-12-28 | Done
776 | 2025-12-28 | 13 | 61 | MotorOverCur | Reset the tracker | 2025-12-28 | Done
777 | 2025-12-28 | 41 | 32 | no communication | Reset the tracker | 2025-12-28 | Done
778 | 2025-12-28 | 76 | 106 | no communication | Reset the tracker | 2025-12-28 | Done
779 | 2025-12-28 | 83 | 143 | MotorOverCur | Reset the tracker | 2025-12-28 | Done
780 | 2025-12-28 | 104 | 34 | MotorReversal | Reset the tracker | 2025-12-28 | Done
781 | 2025-12-28 | 104 | 40 | MotorReversal | Reset the tracker | 2025-12-28 | Done
782 | 2025-12-28 | 106 | 94 | no communication | Reset the tracker | 2025-12-28 | Done
783 | 2025-12-29 | 37 | 27 | AngleNoCom | Rectified | 2026-01-01 | Done | Transmission shaft damage
784 | 2025-12-29 | 119 | 72 | MotorOverCur | Replaced | 2026-01-01 | Done | Gaskit missing
785 | 2025-12-29 | 7 | 74 | BatSOCLow | Reset the Tracker | 2025-12-29 | Done
786 | 2025-12-29 | 29 | 32 | AngleNoChg | Reset the Tracker | 2025-12-29 | Done
787 | 2025-12-29 | 50 | 36 | no communication | Reset the Tracker | 2025-12-29 | Done
788 | 2025-12-29 | 56 | 9 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
789 | 2025-12-29 | 56 | 11 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
790 | 2025-12-29 | 56 | 12 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
791 | 2025-12-29 | 56 | 33 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
792 | 2025-12-29 | 56 | 55 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
793 | 2025-12-29 | 56 | 57 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
794 | 2025-12-29 | 56 | 58 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
795 | 2025-12-29 | 56 | 62 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
796 | 2025-12-29 | 56 | 83 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
797 | 2025-12-29 | 56 | 99 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
798 | 2025-12-29 | 56 | 108 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
799 | 2025-12-29 | 56 | 128 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
800 | 2025-12-29 | 56 | 131 | BatSOCLow | Reset the tracker | 2025-12-29 | Done
801 | 2025-12-29 | 59 | 103 | EmergencyStop | Emergency released | 2025-12-29 | Done
802 | 2025-12-29 | 62 | 35 | EmergencyStop | Emergency released | 2025-12-29 | Done
803 | 2025-12-29 | 64 | 20 | EmergencyStop | Emergency released | 2025-12-29 | Done
804 | 2025-12-29 | 81 | 66 | AngleNoChg | Reset the Tracker | 2025-12-29 | Done
805 | 2025-12-29 | 91 | 36 | EmergencyStop | Emergency released | 2025-12-29 | Done
806 | 2025-12-29 | 91 | 110 | BatSOCLow | Reset the Tracker | 2025-12-29 | Done
807 | 2025-12-29 | 107 | 55 | no communication | Reset the Tracker | 2025-12-29 | Done
808 | 2025-12-29 | 119 | 49 | no communication | Reset the Tracker | 2025-12-29 | Done
809 | 2025-12-30 | 19 | 20 | MotorOverCur | Reset the Tracker | 2025-12-30 | Done
810 | 2025-12-30 | 29 | 33 | AngleNoChg | Reset the Tracker | 2025-12-30 | Done
811 | 2025-12-30 | 43 | 18 | MotorOverCur | Reset the Tracker | 2025-12-30 | Done
812 | 2025-12-30 | 56 | 125 | EmergencyStop | Emergency released | 2025-12-30 | Done
813 | 2025-12-30 | 64 | 101 | BatError | Reset the Tracker | 2025-12-30 | Done
814 | 2025-12-30 | 66 | 148 | AngleNoChg | Reset the Tracker | 2025-12-30 | Done
815 | 2025-12-30 | 74 | 10 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
816 | 2025-12-30 | 74 | 19 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
817 | 2025-12-30 | 74 | 21 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
818 | 2025-12-30 | 74 | 23 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
819 | 2025-12-30 | 74 | 31 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
820 | 2025-12-30 | 74 | 33 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
821 | 2025-12-30 | 74 | 35 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
822 | 2025-12-30 | 74 | 116 | MotorReversal | Reset the Tracker | 2025-12-30 | Done
823 | 2025-12-30 | 74 | 128 | EmergencyStop | Emergency released | 2025-12-30 | Done
824 | 2025-12-30 | 74 | 130 | EmergencyStop | Emergency released | 2025-12-30 | Done
825 | 2025-12-30 | 86 | 109 | no communication | Reset the Tracker | 2025-12-30 | Done
826 | 2025-12-31 | 58 | 111 | no communication | Rectified | 2026-01-01 | Done | DC Power issue
827 | 2025-12-31 | 64 | 20 | EmergencyStop | Rectified | 2026-01-02 | Done | Allignment issue
828 | 2025-12-31 | 23 | 133 | AngleNoChg | Replaced | 2026-01-03 | Done | Transmission shaft damagae
829 | 2025-12-31 | 7 | 74 | BatSOCLow | Reset the Tracker | 2025-12-31 | Done
830 | 2025-12-31 | 61 | 58 | EmergencyStop | Emergency released | 2025-12-31 | Done
831 | 2025-12-31 | 64 | 101 | BatSOCLow | Reset the Tracker | 2025-12-31 | Done
832 | 2025-12-31 | 74 | 72 | no communication | Reset the Tracker | 2025-12-31 | Done
833 | 2025-12-31 | 121 | 64 | MotorReversal | Reset the Tracker | 2025-12-31 | Done
834 | 2026-01-01 | 61 | 58 | EmergencyStop | Emergency released | 2026-01-01 | Done
835 | 2026-01-01 | 65 | 53 | AngleNoChg | Reset the Tracker | 2026-01-01 | Done
836 | 2026-01-01 | 66 | 128 | AngleNoChg | Reset the Tracker | 2026-01-01 | Done
837 | 2026-01-01 | 66 | 132 | MotorReversal | Reset the Tracker | 2026-01-01 | Done
838 | 2026-01-01 | 91 | 110 | BatSOCLow | Reset the Tracker | 2026-01-01 | Done
839 | 2026-01-02 | 115 | 12 | MotorOverCur | Replaced | 2026-01-04 | Done | Transmission shaft damage
840 | 2026-01-02 | 122 | 125 | AngleNoChg | Replaced | 2026-01-04 | Done | Gasket Missing
841 | 2026-01-02 | 23 | 16 | no communication | Reset the Tracker | 2026-01-02 | Done
842 | 2026-01-02 | 28 | 5 | MotorOverCur | Reset the Tracker | 2026-01-02 | Done
843 | 2026-01-02 | 29 | 33 | MotorOverCur | Reset the Tracker | 2026-01-02 | Done
844 | 2026-01-02 | 56 | 51 | BatSOCLow | Reset the Tracker | 2026-01-02 | Done
845 | 2026-01-02 | 66 | 35 | BatSOCLow | Reset the Tracker | 2026-01-02 | Done
846 | 2026-01-02 | 66 | 87 | MotorReversal | Reset the Tracker | 2026-01-02 | Done
847 | 2026-01-02 | 66 | 99 | BatSOCLow | Reset the Tracker | 2026-01-02 | Done
848 | 2026-01-02 | 70 | 15 | no communication | Reset the Tracker | 2026-01-02 | Done
849 | 2026-01-02 | 74 | 118 | AngleNoChg | Reset the Tracker | 2026-01-02 | Done
850 | 2026-01-02 | 74 | 125 | no communication | Reset the Tracker | 2026-01-02 | Done
851 | 2026-01-02 | 76 | 106 | AngleNoChg | Reset the Tracker | 2026-01-02 | Done
852 | 2026-01-02 | 80 | 55 | no communication | Reset the Tracker | 2026-01-02 | Done
853 | 2026-01-02 | 91 | 36 | BatSOCLow | Reset the Tracker | 2026-01-02 | Done
854 | 2026-01-02 | 91 | 110 | BatSOCLow | Reset the Tracker | 2026-01-02 | Done
855 | 2025-01-03 | 53 | 113 | EmergencyStop | Rectified | 2025-01-03 | Done | Alignment Issue
856 | 2026-01-03 | 66 | 48 | BatSOCLow | Reset the Tracker | 2025-01-03 | Done
857 | 2026-01-03 | 66 | 87 | BatSOCLow | Reset the Tracker | 2025-01-03 | Done
858 | 2026-01-04 | 37 | 39 | EmergencyStop | Replaced | 2026-01-06 | Done | Transmission shaft damage
859 | 2026-01-04 | 58 | 76 | EmergencyStop | Rectified | 2026-01-05 | Done | Alignment issue
860 | 2026-01-04 | 59 | 77 | AngleNoChg | Replaced | 2026-01-05 | Done | Transmission shaft damage
861 | 2026-01-04 | 28 | 5 | MotorOverCur | Reset the Tracker | 2026-01-04 | Done
862 | 2026-01-04 | 56 | 12 | BatSOCLow | Reset the Tracker | 2026-01-04 | Done
863 | 2026-01-04 | 56 | 108 | BatSOCLow | Reset the Tracker | 2026-01-04 | Done
864 | 2026-01-04 | 66 | 87 | BatSOCLow | Reset the Tracker | 2026-01-04 | Done
865 | 2026-01-04 | 128 | 72 | EmergencyStop | Emergency released | 2026-01-04 | Done
866 | 2026-01-05 | 6 | 136 | MotorOverCur | Reset the Tracker | 2026-01-05 | Done
867 | 2026-01-05 | 32 | 121 | no communication | Reset the Tracker | 2026-01-05 | Done
868 | 2026-01-05 | 36 | 139 | no communication | Reset the Tracker | 2026-01-05 | Done
869 | 2026-01-05 | 56 | 12 | BatSOCLow | Reset the Tracker | 2026-01-05 | Done
870 | 2026-01-05 | 56 | 27 | MotorReversal | Reset the Tracker | 2026-01-05 | Done
871 | 2026-01-05 | 56 | 29 | MotorReversal | Reset the Tracker | 2026-01-05 | Done
872 | 2026-01-05 | 56 | 32 | MotorReversal | Reset the Tracker | 2026-01-05 | Done
873 | 2026-01-05 | 66 | 132 | no communication | Reset the Tracker | 2026-01-05 | Done
874 | 2026-01-05 | 74 | 52 | no communication | Reset the Tracker | 2026-01-05 | Done
875 | 2026-01-05 | 81 | 123 | no communication | Reset the Tracker | 2026-01-05 | Done
876 | 2026-01-05 | 87 | 93 | no communication | Reset the Tracker | 2026-01-05 | Done
877 | 2026-01-05 | 91 | 36 | BatSOCLow | Reset the Tracker | 2026-01-05 | Done
878 | 2026-01-05 | 99 | 107 | no communication | Reset the Tracker | 2026-01-05 | Done
879 | 2026-01-05 | 99 | 115 | no communication | Reset the Tracker | 2026-01-05 | Done
880 | 2026-01-05 | 99 | 136 | no communication | Reset the Tracker | 2026-01-05 | Done
881 | 2026-01-05 | 106 | 70 | no communication | Reset the Tracker | 2026-01-05 | Done
882 | 2026-01-05 | 112 | 83 | no communication | Reset the Tracker | 2026-01-05 | Done
883 | 2026-01-05 | 112 | 106 | no communication | Reset the Tracker | 2026-01-05 | Done
884 | 2026-01-05 | 124 | 24 | no communication | Reset the Tracker | 2026-01-05 | Done
885 | 2026-01-05 | 95 | 92 | AngleNoChg | Replaced | 2026-01-10 | Done | Transmission shaft damage
886 | 2026-01-05 | 96 | 1 | AngleNoChg | Replaced | 2026-01-06 | Done | Transmission shaft damage
887 | 2026-01-05 | 119 | 133 | MotorOverCur | Replaced | 2026-01-05 | Done | Transmission shaft damage
888 | 2026-01-06 | 28 | 5 | MotorOverCur | Reset the Tracker | 2026-01-06 | Done
889 | 2026-01-06 | 38 | 92 | no communication | Reset the Tracker | 2026-01-06 | Done
890 | 2026-01-06 | 56 | 11 | no communication | Reset the Tracker | 2026-01-06 | Done
891 | 2026-01-06 | 87 | 108 | AngleNoChg | Reset the Tracker | 2026-01-06 | Done
892 | 2026-01-06 | 37 | 126 | AngleNoChg | Reset the Tracker | 2026-01-06 | Done
893 | 2026-01-07 | 106 | 88 | MotorOverCur | Replaced | 2026-01-09 | Done | Transmission shaft damage
894 | 2026-01-07 | 28 | 5 | MotorOverCur | Reset the Tracker | 2026-01-07 | Done
895 | 2026-01-07 | 43 | 18 | AngleNoChg | Reset the Tracker | 2026-01-07 | Done
896 | 2026-01-07 | 82 | 30 | BatSOCLow | Reset the Tracker | 2026-01-07 | Done
897 | 2026-01-07 | 82 | 73 | BatSOCLow | Reset the Tracker | 2026-01-07 | Done
898 | 2026-01-07 | 128 | 25 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
899 | 2026-01-07 | 128 | 27 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
900 | 2026-01-07 | 128 | 29 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
901 | 2026-01-07 | 128 | 31 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
902 | 2026-01-07 | 128 | 33 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
903 | 2026-01-07 | 128 | 35 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
904 | 2026-01-07 | 128 | 43 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
905 | 2026-01-07 | 128 | 45 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
906 | 2026-01-07 | 128 | 53 | MotorReversal | Reset the Tracker | 2026-01-07 | Done
907 | 2026-01-07 | 91 | 36 | AngleNoChg | Reset the Tracker | 2026-01-07 | Done
908 | 2026-01-07 | 103 | 83 | no communication | Reset the Tracker | 2026-01-07 | Done
909 | 2026-01-08 | 20 | 68 | no communication | Reset the Tracker | 2026-01-08 | Done
910 | 2026-01-08 | 56 | 106 | EmergencyStop | Emergency released | 2026-01-08 | Done
911 | 2026-01-08 | 66 | 12 | MotorReversal | Reset the Tracker | 2026-01-08 | Done
912 | 2026-01-08 | 74 | 12 | no communication | Reset the Tracker | 2026-01-08 | Done
913 | 2026-01-08 | 82 | 73 | BatSOCLow | Reset the Tracker | 2026-01-08 | Done
914 | 2026-01-08 | 91 | 36 | BatSOCLow | Reset the Tracker | 2026-01-08 | Done
915 | 2026-01-08 | 30 | 87 | MotorOverCur | Reset the Tracker | 2026-01-08 | Done
916 | 2026-01-08 | 37 | 126 | AngleNoChg | Reset the Tracker | 2026-01-08 | Done
917 | 2026-01-08 | 76 | 106 | no communication | Reset the Tracker | 2026-01-08 | Done
918 | 2026-01-08 | 80 | 28 | no communication | Reset the Tracker | 2026-01-08 | Done
919 | 2026-01-09 | 37 | 126 | AngleNoChg | Reset the Tracker | 2026-01-09 | Done
920 | 2026-01-09 | 56 | 45 | no communication | Reset the Tracker | 2026-01-09 | Done
921 | 2026-01-10 | 20 | 68 | no communication | Reset the Tracker | 2026-01-10 | Done
922 | 2026-01-10 | 31 | 21 | BatSOCLow | Reset the Tracker | 2026-01-10 | Done
923 | 2026-01-10 | 80 | 110 | no communication | Reset the Tracker | 2026-01-10 | Done
924 | 2026-01-10 | 82 | 73 | BatSOCLow | Reset the Tracker | 2026-01-10 | Done
925 | 2026-01-11 | 56 | 39 | AngleNoCom | Reset the Tracker | 2026-01-11 | Done
926 | 2026-01-11 | 59 | 79 | AngleNoChg | Replaced | 2026-01-12 | Done | Transmisison shaft damage
927 | 2026-01-11 | 91 | 36 | BatSOCLow | Reset the Tracker | 2026-01-11 | Done
928 | 2026-01-11 | 37 | 71 | Stop | Rectified | 2026-01-12 | Done | Alignment issue
929 | 2026-01-11 | 37 | 126 | Stop | Replaced | 2026-01-12 | Done | TT Bearing damage
930 | 2026-01-11 | 63 | 87 | Stop | Replaced | 2026-01-12 | Done | TT Bearing damage
931 | 2026-01-12 | 132 | 53 | BatSOCLow | Reset the Tracker | 2026-01-12 | Done
932 | 2026-01-12 | 19 | 59 | MotorOverCur | Replaced | 2026-01-13 | Done | TT Bearing damage
933 | 2026-01-12 | 48 | 15 | MotorOverCur | Replaced | 2026-01-13 | Done | Gaskit missing
934 | 2026-01-14 | 19 | 59 | MotorOverCur | Reset the Tracker | 2026-01-14 | Done
935 | 2026-01-14 | 128 | 2 | EmergencyStop | Reset the Tracker | 2026-01-14 | Done
936 | 2026-01-14 | 128 | 116 | EmergencyStop | Reset the Tracker | 2026-01-14 | Done
937 | 2026-01-15 | 74 | 27 | no communication | Reset the Tracker | 2026-01-15 | Done
938 | 2026-01-16 | 4 | 35 | BatSOCLow | Reset the Tracker | 2026-01-17 | Done
939 | 2026-01-16 | 14 | 71 | no communication | Reset the Tracker | 2026-01-17 | Done
940 | 2026-01-16 | 14 | 103 | AngleNoChg | Reset the Tracker | 2026-01-17 | Done
941 | 2026-01-16 | 22 | 44 | no communication | Reset the Tracker | 2026-01-17 | Done
942 | 2026-01-16 | 22 | 62 | no communication | Reset the Tracker | 2026-01-17 | Done
943 | 2026-01-16 | 22 | 105 | no communication | Reset the Tracker | 2026-01-17 | Done
944 | 2026-01-16 | 22 | 108 | no communication | Reset the Tracker | 2026-01-17 | Done
945 | 2026-01-16 | 23 | 16 | no communication | Reset the Tracker | 2026-01-17 | Done
946 | 2026-01-16 | 23 | 22 | no communication | Reset the Tracker | 2026-01-17 | Done
947 | 2026-01-16 | 26 | 36 | no communication | Reset the Tracker | 2026-01-17 | Done
948 | 2026-01-16 | 26 | 61 | no communication | Reset the Tracker | 2026-01-17 | Done
949 | 2026-01-16 | 26 | 131 | no communication | Reset the Tracker | 2026-01-17 | Done
950 | 2026-01-16 | 31 | 20 | no communication | Reset the Tracker | 2026-01-17 | Done
951 | 2026-01-16 | 36 | 72 | no communication | Reset the Tracker | 2026-01-17 | Done
952 | 2026-01-16 | 42 | 107 | no communication | Reset the Tracker | 2026-01-17 | Done
953 | 2026-01-16 | 50 | 24 | no communication | Reset the Tracker | 2026-01-17 | Done
954 | 2026-01-16 | 50 | 36 | no communication | Reset the Tracker | 2026-01-17 | Done
955 | 2026-01-16 | 56 | 120 | BatSOCLow | Reset the Tracker | 2026-01-17 | Done
956 | 2026-01-16 | 57 | 63 | no communication | Reset the Tracker | 2026-01-17 | Done
957 | 2026-01-16 | 67 | 27 | no communication | Reset the Tracker | 2026-01-17 | Done
958 | 2026-01-16 | 68 | 137 | no communication | Reset the Tracker | 2026-01-17 | Done
959 | 2026-01-16 | 70 | 26 | no communication | Reset the Tracker | 2026-01-17 | Done
960 | 2026-01-16 | 70 | 38 | no communication | Reset the Tracker | 2026-01-17 | Done
961 | 2026-01-16 | 70 | 43 | no communication | Reset the Tracker | 2026-01-17 | Done
962 | 2026-01-16 | 70 | 47 | no communication | Reset the Tracker | 2026-01-17 | Done
963 | 2026-01-16 | 70 | 55 | no communication | Reset the Tracker | 2026-01-17 | Done
964 | 2026-01-16 | 70 | 59 | no communication | Reset the Tracker | 2026-01-17 | Done
965 | 2026-01-16 | 70 | 61 | no communication | Reset the Tracker | 2026-01-17 | Done
966 | 2026-01-16 | 70 | 63 | no communication | Reset the Tracker | 2026-01-17 | Done
967 | 2026-01-16 | 70 | 92 | no communication | Reset the Tracker | 2026-01-17 | Done
968 | 2026-01-16 | 70 | 94 | no communication | Reset the Tracker | 2026-01-17 | Done
969 | 2026-01-16 | 79 | 84 | no communication | Reset the Tracker | 2026-01-17 | Done
970 | 2026-01-16 | 80 | 134 | no communication | Reset the Tracker | 2026-01-17 | Done
971 | 2026-01-16 | 90 | 117 | no communication | Reset the Tracker | 2026-01-17 | Done
972 | 2026-01-16 | 94 | 134 | no communication | Reset the Tracker | 2026-01-17 | Done
973 | 2026-01-16 | 95 | 3 | no communication | Reset the Tracker | 2026-01-17 | Done
974 | 2026-01-16 | 95 | 66 | no communication | Reset the Tracker | 2026-01-17 | Done
975 | 2026-01-16 | 95 | 135 | no communication | Reset the Tracker | 2026-01-17 | Done
976 | 2026-01-16 | 107 | 55 | no communication | Reset the Tracker | 2026-01-17 | Done
977 | 2026-01-16 | 109 | 21 | no communication | Reset the Tracker | 2026-01-17 | Done
978 | 2026-01-16 | 109 | 39 | no communication | Reset the Tracker | 2026-01-17 | Done
979 | 2026-01-16 | 122 | 83 | no communication | Reset the Tracker | 2026-01-17 | Done
980 | 2026-01-16 | 128 | 99 | no communication | Reset the Tracker | 2026-01-17 | Done
981 | 2026-01-17 | 14 | 103 | AngleNoChg | Replaced | 2026-01-18 | Done | Transmission shaft damage
982 | 2026-01-17 | 42 | 107 | no communication | Reset the Tracker | 2026-01-17 | Done
983 | 2026-01-17 | 50 | 36 | no communication | Reset the Tracker | 2026-01-17 | Done
984 | 2026-01-17 | 55 | 96 | no communication | Reset the Tracker | 2026-01-17 | Done
985 | 2026-01-17 | 57 | 63 | no communication | Reset the Tracker | 2026-01-17 | Done
986 | 2026-01-17 | 60 | 91 | no communication | Reset the Tracker | 2026-01-17 | Done
987 | 2026-01-17 | 67 | 27 | no communication | Reset the Tracker | 2026-01-17 | Done
988 | 2026-01-17 | 74 | 112 | AngleNoChg | Reset the Tracker | 2026-01-17 | Done
989 | 2026-01-17 | 89 | 119 | no communication | Reset the Tracker | 2026-01-17 | Done
990 | 2026-01-17 | 90 | 117 | no communication | Reset the Tracker | 2026-01-17 | Done
991 | 2026-01-17 | 101 | 83 | Stop | Reset the Tracker | 2026-01-17 | Done
992 | 2026-01-17 | 106 | 30 | no communication | Reset the Tracker | 2026-01-17 | Done
993 | 2026-01-17 | 107 | 55 | no communication | Reset the Tracker | 2026-01-17 | Done
994 | 2026-01-17 | 24 | 35 | AngleNoChg | Replaced | 2026-01-18 | Done | Transmission shaft damage
995 | 2026-01-18 | 60 | 91 | no communication | Reset the Tracker | 2026-01-18 | Done
996 | 2026-01-18 | 89 | 119 | no communication | Reset the Tracker | 2026-01-18 | Done
997 | 2026-01-18 | 100 | 123 | no communication | Reset the Tracker | 2026-01-18 | Done
998 | 2026-01-18 | 104 | 55 | no communication | Reset the Tracker | 2026-01-18 | Done
999 | 2026-01-18 | 3 | 103 | EmergencyStop | Replaced | 2026-01-19 | Done | Transmission Shaft Twisted
1000 | 2026-01-19 | 66 | 132 | no communication | Reset the Tracker | 2026-01-19 | Done
1001 | 2026-01-19 | 75 | 76 | no communication | Reset the Tracker | 2026-01-19 | Done
1002 | 2026-01-19 | 131 | 68 | no communication | Reset the Tracker | 2026-01-19 | Done
1003 | 2026-01-19 | 77 | 3 | MotorOverCur | Replaced | 2026-01-20 | Done | Transmission shaft damage
1004 | 2026-01-20 | 63 | 38 | no communication | Reset the Tracker | 2026-01-20 | Done
1005 | 2026-01-20 | 70 | 69 | no communication | Reset the Tracker | 2026-01-20 | Done
1006 | 2026-01-20 | 74 | 10 | no communication | Reset the Tracker | 2026-01-20 | Done
1007 | 2026-01-20 | 74 | 39 | no communication | Reset the Tracker | 2026-01-20 | Done
1008 | 2026-01-20 | 74 | 52 | no communication | Reset the Tracker | 2026-01-20 | Done
1009 | 2026-01-20 | 80 | 80 | BatSOCLow | Reset the Tracker | 2026-01-20 | Done
1010 | 2026-01-20 | 87 | 74 | no communication | Reset the Tracker | 2026-01-20 | Done
1011 | 2026-01-20 | 87 | 93 | no communication | Reset the Tracker | 2026-01-20 | Done
1012 | 2026-01-20 | 99 | 115 | no communication | Reset the Tracker | 2026-01-20 | Done
1013 | 2026-01-20 | 99 | 136 | no communication | Reset the Tracker | 2026-01-20 | Done
1014 | 2026-01-20 | 112 | 93 | no communication | Reset the Tracker | 2026-01-20 | Done
1015 | 2026-01-20 | 116 | 104 | no communication | Reset the Tracker | 2026-01-20 | Done
1016 | 2026-01-21 | 54 | 74 | no communication | Reset the Tracker | 2026-01-21 | Done
1017 | 2026-01-21 | 114 | 138 | no communication | Reset the Tracker | 2026-01-21 | Done
1018 | 2026-01-21 | 124 | 66 | no communication | Reset the Tracker | 2026-01-21 | Done
1019 | 2026-01-21 | 19 | 32 | MotorOverCur | Reset the Tracker | 2026-01-21 | Done
1020 | 2026-01-21 | 80 | 29 | no communication | Reset the Tracker | 2026-01-21 | Done
1021 | 2026-01-21 | 53 | 62 | MotorOverCur | Replaced | 2026-01-22 | Done | Transmission shaft damage
1022 | 2026-01-22 | 66 | 132 | no communication | Reset the Tracker | 2026-01-22 | Done
1023 | 2026-01-22 | 74 | 52 | no communication | Reset the Tracker | 2026-01-22 | Done
1024 | 2026-01-22 | 74 | 55 | no communication | Reset the Tracker | 2026-01-22 | Done
1025 | 2026-01-22 | 128 | 57 | no communication | Reset the Tracker | 2026-01-22 | Done
1026 | 2026-01-22 | 131 | 4 | no communication | Reset the Tracker | 2026-01-22 | Done
1027 | 2026-01-22 | 131 | 14 | no communication | Reset the Tracker | 2026-01-22 | Done
1028 | 2026-01-23 | 67 | 28 | BatSOCLow | Reset the Tracker | 2026-01-23 | Done
1029 | 2026-01-23 | 99 | 115 | no communication | Reset the Tracker | 2026-01-23 | Done
1030 | 2026-01-23 | 99 | 136 | no communication | Reset the Tracker | 2026-01-23 | Done
1031 | 2026-01-23 | 4 | 35 | BatSOCLow | Reset the Tracker | 2026-01-23 | Done
1032 | 2026-01-23 | 67 | 28 | EmergencyStop | Replaced | 2026-01-25 | Done | Transmission shaft damage
1033 | 2026-01-25 | 28 | 103 | no communication | Reset the Tracker | 2026-01-25 | Done
1034 | 2026-01-25 | 42 | 31 | no communication | Reset the Tracker | 2026-01-25 | Done
1035 | 2026-01-25 | 70 | 12 | no communication | Reset the Tracker | 2026-01-25 | Done
1036 | 2026-01-25 | 70 | 19 | no communication | Reset the Tracker | 2026-01-25 | Done
1037 | 2026-01-25 | 70 | 43 | no communication | Reset the Tracker | 2026-01-25 | Done
1038 | 2026-01-25 | 70 | 53 | no communication | Reset the Tracker | 2026-01-25 | Done
1039 | 2026-01-25 | 123 | 135 | no communication | Reset the Tracker | 2026-01-25 | Done
1040 | 2026-01-26 | 12 | 69 | no communication | Reset the Tracker | 2026-01-26 | Done
1041 | 2026-01-26 | 15 | 96 | no communication | Reset the Tracker | 2026-01-26 | Done
1042 | 2026-01-26 | 17 | 94 | no communication | Reset the Tracker | 2026-01-26 | Done
1043 | 2026-01-26 | 70 | 35 | no communication | Reset the Tracker | 2026-01-26 | Done
1044 | 2026-01-26 | 95 | 67 | BatSOCLow | Reset the Tracker | 2026-01-26 | Done
1045 | 2026-01-26 | 95 | 90 | no communication | Reset the Tracker | 2026-01-26 | Done
1046 | 2026-01-26 | 99 | 136 | no communication | Reset the Tracker | 2026-01-26 | Done
1047 | 2026-01-26 | 109 | 69 | no communication | Reset the Tracker | 2026-01-26 | Done
1048 | 2026-01-26 | 114 | 120 | no communication | Reset the Tracker | 2026-01-26 | Done
1049 | 2026-01-26 | 66 | 60 | AngleNoChg | Replaced | 2026-01-27 | Done | Gaskit Missing
1050 | 2026-01-27 | 42 | 31 | no communication | Reset the tracker | 2026-01-27 | Done
1051 | 2026-01-27 | 70 | 43 | no communication | Reset the tracker | 2026-01-27 | Done
1052 | 2026-01-27 | 101 | 105 | no communication | Reset the tracker | 2026-01-27 | Done
1053 | 2026-01-28 | 9 | 105 | AngleNoChg | Replaced | 2026-01-29 | Done | Transmission shaft damage
1054 | 2026-01-28 | 80 | 46 | no communication | Reset the tracker | 2026-01-28 | Done
1055 | 2026-01-28 | 80 | 80 | no communication | Reset the tracker | 2026-01-28 | Done
1056 | 2026-01-28 | 89 | 51 | no communication | Reset the tracker | 2026-01-28 | Done
1057 | 2026-01-28 | 95 | 3 | no communication | Reset the tracker | 2026-01-28 | Done
1058 | 2026-01-28 | 99 | 9 | BatError | Reset the tracker | 2026-01-28 | Done
1059 | 2026-01-28 | 108 | 77 | no communication | Reset the tracker | 2026-01-28 | Done
1060 | 2026-01-28 | 109 | 39 | no communication | Reset the tracker | 2026-01-28 | Done
1061 | 2026-01-28 | 117 | 121 | MotorOverCur | Reset the tracker | 2026-01-28 | Done
1062 | 2026-01-29 | 16 | 116 | AngleNoCom | Replaced | 2026-02-01 | Done | Transmission shaft damage
1063 | 2026-01-29 | 19 | 60 | BatSOCLow | Reset the tracker | 2026-01-29 | Done
1064 | 2026-01-29 | 19 | 104 | no communication | Reset the tracker | 2026-01-29 | Done
1065 | 2026-01-29 | 58 | 45 | AngleNoChg | Replaced | 2026-01-31 | Done | Transmission shaft damage
1066 | 2026-01-29 | 89 | 139 | no communication | Reset the tracker | 2026-01-29 | Done
1067 | 2026-01-29 | 95 | 15 | no communication | Reset the tracker | 2026-01-29 | Done
1068 | 2026-01-29 | 101 | 113 | EmergencyStop | Emergency Released | 2026-01-29 | Done
1069 | 2026-01-30 | 22 | 44 | no communication | Reset the tracker | 2026-01-30 | Done
1070 | 2026-01-30 | 30 | 21 | no communication | Reset the tracker | 2026-01-30 | Done
1071 | 2026-01-30 | 43 | 18 | AngleNoChg | Reset the tracker | 2026-01-30 | Done
1072 | 2026-01-30 | 50 | 24 | no communication | Reset the tracker | 2026-01-30 | Done
1073 | 2026-01-30 | 50 | 36 | no communication | Reset the tracker | 2026-01-30 | Done
1074 | 2026-01-30 | 54 | 74 | MotorReversal | Reset the tracker | 2026-01-30 | Done
1075 | 2026-01-30 | 55 | 97 | no communication | Reset the tracker | 2026-01-30 | Done
1076 | 2026-01-30 | 60 | 91 | no communication | Reset the tracker | 2026-01-30 | Done
1077 | 2026-01-30 | 99 | 5 | BatError | Reset the tracker | 2026-01-30 | Done
1078 | 2026-01-30 | 114 | 102 | no communication | Reset the tracker | 2026-01-30 | Done
1079 | 2026-01-31 | 54 | 74 | no communication | Reset the Tracker | 2026-01-31 | Done
1080 | 2026-01-31 | 74 | 24 | no communication | Reset the Tracker | 2026-01-31 | Done
1081 | 2026-01-31 | 74 | 59 | no communication | Reset the Tracker | 2026-01-31 | Done
1082 | 2026-01-31 | 74 | 72 | no communication | Reset the Tracker | 2026-01-31 | Done
1083 | 2026-01-31 | 114 | 102 | no communication | Reset the Tracker | 2026-01-31 | Done
1084 | 2026-02-01 | 35 | 71 | MotorReversal | Reset the Tracker | 2026-02-01 | Done
1085 | 2026-02-01 | 50 | 24 | no communication | Reset the Tracker | 2026-02-01 | Done
1086 | 2026-02-01 | 50 | 36 | no communication | Reset the Tracker | 2026-02-01 | Done
1087 | 2026-02-01 | 54 | 104 | no communication | Reset the Tracker | 2026-02-01 | Done
1088 | 2026-02-01 | 54 | 112 | no communication | Reset the Tracker | 2026-02-01 | Done
1089 | 2026-02-01 | 54 | 114 | no communication | Reset the Tracker | 2026-02-01 | Done
1090 | 2026-02-01 | 54 | 116 | no communication | Reset the Tracker | 2026-02-01 | Done
1091 | 2026-02-01 | 65 | 114 | EmergencyStop | Emergency Released | 2026-02-01 | Done
1092 | 2026-02-01 | 68 | 137 | no communication | Reset the Tracker | 2026-02-01 | Done
1093 | 2026-02-01 | 70 | 24 | no communication | Reset the Tracker | 2026-02-01 | Done
1094 | 2026-02-01 | 70 | 34 | no communication | Reset the Tracker | 2026-02-01 | Done
1095 | 2026-02-01 | 70 | 38 | no communication | Reset the Tracker | 2026-02-01 | Done
1096 | 2026-02-01 | 70 | 43 | no communication | Reset the Tracker | 2026-02-01 | Done
1097 | 2026-02-01 | 90 | 99 | no communication | Reset the Tracker | 2026-02-01 | Done
1098 | 2026-02-01 | 94 | 105 | no communication | Reset the Tracker | 2026-02-01 | Done
1099 | 2026-02-01 | 94 | 128 | no communication | Reset the Tracker | 2026-02-01 | Done
1100 | 2026-02-01 | 101 | 26 | no communication | Reset the Tracker | 2026-02-01 | Done
1101 | 2026-02-01 | 4 | 98 | BatSOCLow | Reset the Tracker | 2026-02-01 | Done
1102 | 2026-02-01 | 34 | 119 | no communication | Reset the Tracker | 2026-02-01 | Done
1103 | 2026-02-02 | 11 | 108 | BatSOCLow | Reset the Tracker | 2026-02-02 | Done
1104 | 2026-02-02 | 54 | 112 | no communication | Reset the Tracker | 2026-02-02 | Done
1105 | 2026-02-02 | 94 | 125 | no communication | Reset the Tracker | 2026-02-02 | Done
1106 | 2026-02-03 | 38 | 115 | BatSOCLow | Reset the Tracker | 2026-02-03 | Done
1107 | 2026-02-03 | 38 | 146 | EmergencyStop | Emergency Released | 2026-02-03 | Done
1108 | 2026-02-03 | 46 | 13 | EmergencyStop | Emergency Released | 2026-02-03 | Done
1109 | 2026-02-03 | 70 | 20 | no communication | Reset the Tracker | 2026-02-03 | Done
1110 | 2026-02-03 | 70 | 26 | no communication | Reset the Tracker | 2026-02-03 | Done
1111 | 2026-02-03 | 70 | 43 | no communication | Reset the Tracker | 2026-02-03 | Done
1112 | 2026-02-03 | 108 | 138 | no communication | Reset the Tracker | 2026-02-03 | Done
1113 | 2026-02-03 | 109 | 39 | no communication | Reset the Tracker | 2026-02-03 | Done
1114 | 2026-02-03 | 123 | 135 | no communication | Reset the Tracker | 2026-02-03 | Done
1115 | 2026-02-04 | 2 | 11 | no communication | Reset the Tracker | 2026-02-04 | Done
1116 | 2026-02-04 | 21 | 29 | no communication | Reset the Tracker | 2026-02-04 | Done
1117 | 2026-02-04 | 42 | 30 | no communication | Reset the Tracker | 2026-02-04 | Done
1118 | 2026-02-04 | 42 | 31 | no communication | Reset the Tracker | 2026-02-04 | Done
1119 | 2026-02-04 | 50 | 24 | no communication | Reset the Tracker | 2026-02-04 | Done
1120 | 2026-02-04 | 50 | 36 | no communication | Reset the Tracker | 2026-02-04 | Done
1121 | 2026-02-04 | 54 | 112 | no communication | Reset the Tracker | 2026-02-04 | Done
1122 | 2026-02-04 | 62 | 80 | no communication | Reset the Tracker | 2026-02-04 | Done
1123 | 2026-02-04 | 66 | 25 | no communication | Reset the Tracker | 2026-02-04 | Done
1124 | 2026-02-04 | 66 | 112 | no communication | Reset the Tracker | 2026-02-04 | Done
1125 | 2026-02-04 | 74 | 12 | no communication | Reset the Tracker | 2026-02-04 | Done
1126 | 2026-02-04 | 75 | 76 | no communication | Reset the Tracker | 2026-02-04 | Done
1127 | 2026-02-04 | 95 | 3 | no communication | Reset the Tracker | 2026-02-04 | Done
1128 | 2026-02-04 | 99 | 115 | no communication | Reset the Tracker | 2026-02-04 | Done
1129 | 2026-02-04 | 99 | 136 | no communication | Reset the Tracker | 2026-02-04 | Done
1130 | 2026-02-04 | 100 | 123 | no communication | Reset the Tracker | 2026-02-04 | Done
1131 | 2026-02-04 | 101 | 42 | no communication | Reset the Tracker | 2026-02-04 | Done
1132 | 2026-02-04 | 101 | 105 | no communication | Reset the Tracker | 2026-02-04 | Done
1133 | 2026-02-04 | 104 | 9 | no communication | Reset the Tracker | 2026-02-04 | Done
1134 | 2026-02-04 | 110 | 101 | EmergencyStop | Emergency Released | 2026-02-04 | Done
1135 | 2026-02-04 | 110 | 105 | EmergencyStop | Emergency Released | 2026-02-04 | Done
1136 | 2026-02-04 | 112 | 89 | no communication | Reset the Tracker | 2026-02-04 | Done
1137 | 2026-02-04 | 114 | 120 | no communication | Reset the Tracker | 2026-02-04 | Done
1138 | 2026-02-04 | 128 | 124 | no communication | Reset the Tracker | 2026-02-04 | Done
1139 | 2026-02-05 | 14 | 107 | EmergencyStop | Replaced | 2026-02-08 | Done | Transmission shaft damage
1140 | 2026-02-05 | 42 | 31 | no communication | Reset the Tracker | 2026-02-05 | Done
1141 | 2026-02-05 | 42 | 70 | MotorReversal | Reset the Tracker | 2026-02-05 | Done
1142 | 2026-02-05 | 46 | 107 | no communication | Reset the Tracker | 2026-02-05 | Done
1143 | 2026-02-05 | 53 | 119 | AngleNoChg | Replaced | 2026-02-08 | Done | Transmission shaft damage
1144 | 2026-02-05 | 62 | 80 | no communication | Reset the Tracker | 2026-02-05 | Done
1145 | 2026-02-05 | 70 | 43 | no communication | Reset the Tracker | 2026-02-05 | Done
1146 | 2026-02-05 | 80 | 80 | no communication | Reset the Tracker | 2026-02-05 | Done
1147 | 2026-02-05 | 94 | 125 | no communication | Reset the Tracker | 2026-02-05 | Done
1148 | 2026-02-05 | 114 | 102 | no communication | Reset the Tracker | 2026-02-05 | Done
1149 | 2026-02-05 | 123 | 71 | no communication | Reset the Tracker | 2026-02-05 | Done
1150 | 2026-02-06 | 13 | 76 | MotorOverCur | Replaced | 2026-02-08 | Done | TT bearing damage
1151 | 2026-02-06 | 46 | 13 | EmergencyStop | Emergency Released | 2026-02-07 | Done
1152 | 2026-02-06 | 62 | 80 | no communication | Reset the Tracker | 2026-02-06 | Done
1153 | 2026-02-06 | 109 | 39 | no communication | Reset the Tracker | 2026-02-06 | Done
1154 | 2026-02-07 | 9 | 126 | AngleNoChg | Reset the Tracker | 2026-02-07 | Done
1155 | 2026-02-07 | 9 | 132 | AngleNoChg | Reset the Tracker | 2026-02-07 | Done
1156 | 2026-02-07 | 50 | 62 | EmergencyStop | Replaced | 2026-02-15 | Done | Pile Damage
1157 | 2026-02-07 | 58 | 93 | AngleNoChg | Replaced | 2026-02-08 | Done | Transmission shaft damage
1158 | 2026-02-07 | 62 | 80 | no communication | Reset the Tracker | 2026-02-07 | Done
1159 | 2026-02-07 | 109 | 39 | no communication | Reset the Tracker | 2026-02-07 | Done
1160 | 2026-02-07 | 129 | 54 | MotorOverCur | Replaced | 2026-02-08 | Done | Transmission shaft damage
1161 | 2026-02-08 | 14 | 86 | EmergencyStop | Reset the Tracker | 2026-02-08 | Done
1162 | 2026-02-08 | 14 | 88 | EmergencyStop | Reset the Tracker | 2026-02-08 | Done
1163 | 2026-02-08 | 43 | 18 | AngleNoChg | Reset the Tracker | 2026-02-08 | Done
1164 | 2026-02-08 | 70 | 9 | no communication | Reset the Tracker | 2026-02-08 | Done
1165 | 2026-02-08 | 70 | 15 | no communication | Reset the Tracker | 2026-02-08 | Done
1166 | 2026-02-08 | 95 | 2 | no communication | Reset the Tracker | 2026-02-08 | Done
1167 | 2026-02-09 | 23 | 24 | no communication | Reset the Tracker | 2026-02-09 | Done
1168 | 2026-02-09 | 25 | 112 | no communication | Reset the Tracker | 2026-02-09 | Done
1169 | 2026-02-09 | 70 | 51 | no communication | Reset the Tracker | 2026-02-09 | Done
1170 | 2026-02-10 | 2 | 19 | MotorOverCur | Reset the Tracker | 2026-02-10 | Done
1171 | 2026-02-10 | 131 | 108 | MotorOverCur | Replaced | 2026-02-12 | Done | Transmision shaft damage
1172 | 2026-02-11 | 53 | 65 | AngleNoChg | Reset the Tracker | 2026-02-11 | Done
1173 | 2026-02-11 | 59 | 107 | MotorOverCur | Replaced | 2026-02-12 | Done | Transmision shaft damage
1174 | 2026-02-11 | 69 | 5 | BatSOCLow | Reset the Tracker | 2026-02-11 | Done
1175 | 2026-02-11 | 70 | 38 | no communication | Reset the Tracker | 2026-02-11 | Done
1176 | 2026-02-11 | 70 | 53 | no communication | Reset the Tracker | 2026-02-11 | Done
1177 | 2026-02-11 | 98 | 112 | no communication | Reset the Tracker | 2026-02-11 | Done
1178 | 2026-02-12 | 62 | 91 | MotorOverCur | Replaced | 2026-02-14 | Done | Transmision shaft damage
1179 | 2026-02-12 | 77 | 53 | AngleNoChg | Reset the Tracker | 2026-02-12 | Done
1180 | 2026-02-12 | 93 | 66 | no communication | Reset the Tracker | 2026-02-12 | Done
1181 | 2026-02-12 | 121 | 117 | MotorOverCur | Replaced | 2026-02-14 | Done | Transmision shaft damage
1182 | 2026-02-12 | 126 | 77 | MotorOverCur | Replaced | 2026-02-23 | Done | Transmision shaft damage
1183 | 2026-02-12 | 20 | 87 | MotorOverCur | Replaced | 2026-02-14 | Done | Transmision shaft damage
1184 | 2026-02-14 | 58 | 76 | EmergencyStop | Done | 2026-02-15 | Done | Alignment Issue
1185 | 2026-02-14 | 68 | 134 | MotorOverCur | Replaced | 2026-02-15 | Done | Transmision shaft damage
1186 | 2026-02-14 | 73 | 63 | no communication | Reset the Tracker | 2026-02-14 | Done
1187 | 2026-02-14 | 95 | 3 | no communication | Reset the Tracker | 2026-02-14 | Done
1188 | 2026-02-14 | 98 | 112 | no communication | Reset the Tracker | 2026-02-14 | Done
1189 | 2026-02-14 | 11 | 90 | MotorOverCur | Replaced | 2026-02-15 | Done | Transmision shaft damage
1190 | 2026-02-15 | 14 | 111 | EmergencyStop | Reset the Tracker | 2026-02-15 | Done
1191 | 2026-02-15 | 51 | 28 | EmergencyStop | Reset the Tracker | 2026-02-15 | Done
1192 | 2026-02-15 | 68 | 98 | no communication | Reset the Tracker | 2026-02-15 | Done
1193 | 2026-02-15 | 68 | 137 | no communication | Reset the Tracker | 2026-02-15 | Done
1194 | 2026-02-15 | 1 | 73 | BatSOCLow | Reset the Tracker | 2026-02-15 | Done
1195 | 2026-02-16 | 51 | 136 | BatSOCLow | Reset the Tracker | 2026-02-16 | Done
1196 | 2026-02-16 | 94 | 50 | no communication | Reset the Tracker | 2026-02-16 | Done
1197 | 2026-02-16 | 94 | 77 | no communication | Reset the Tracker | 2026-02-16 | Done
1198 | 2026-02-16 | 16 | 1 | MotorOverCur | Replaced | 2026-02-18 | Done | Transmision shaft damage
1199 | 2026-02-17 | 114 | 120 | no communication | Reset the Tracker | 2026-02-17 | Done
1200 | 2026-02-17 | 117 | 4 | no communication | Reset the Tracker | 2026-02-17 | Done
1201 | 2026-02-18 | 62 | 69 | EmergencyStop | Emergency Released | 2026-02-18 | Done
1202 | 2026-02-18 | 71 | 16 | no communication | Reset the Tracker | 2026-02-18 | Done
1203 | 2026-02-18 | 90 | 21 | no communication | Reset the Tracker | 2026-02-18 | Done
1204 | 2026-02-18 | 104 | 9 | no communication | Reset the Tracker | 2026-02-18 | Done
1205 | 2026-02-19 | 15 | 114 | no communication | Reset the Tracker | 2026-02-19 | Done
1206 | 2026-02-19 | 23 | 13 | no communication | Reset the Tracker | 2026-02-19 | Done
1207 | 2026-02-19 | 48 | 67 | BatSOCLow | Reset the Tracker | 2026-02-19 | Done
1208 | 2026-02-19 | 55 | 56 | no communication | Reset the Tracker | 2026-02-19 | Done
1209 | 2026-02-19 | 74 | 104 | AngleNoChg | Reset the Tracker | 2026-02-19 | Done
1210 | 2026-02-19 | 94 | 77 | no communication | Reset the Tracker | 2026-02-19 | Done
1211 | 2026-02-19 | 94 | 128 | no communication | Reset the Tracker | 2026-02-19 | Done
1212 | 2026-02-19 | 114 | 120 | no communication | Reset the Tracker | 2026-02-19 | Done
1213 | 2026-02-21 | 21 | 6 | BatSOCLow | Reset the Tracker | 2026-02-21 | Done
1214 | 2026-02-21 | 21 | 14 | no communication | Reset the Tracker | 2026-02-21 | Done
1215 | 2026-02-21 | 58 | 80 | EmergencyStop | Replaced | 2026-02-23 | Done | Transmision shaft damage
1216 | 2026-02-21 | 66 | 90 | EmergencyStop | Reset the Tracker | 2026-02-21 | Done
1217 | 2026-02-21 | 74 | 10 | no communication | Reset the Tracker | 2026-02-21 | Done
1218 | 2026-02-21 | 74 | 12 | no communication | Reset the Tracker | 2026-02-21 | Done
1219 | 2026-02-21 | 74 | 29 | no communication | Reset the Tracker | 2026-02-21 | Done
1220 | 2026-02-21 | 74 | 55 | no communication | Reset the Tracker | 2026-02-21 | Done
1221 | 2026-02-23 | 1 | 57 | no communication | Reset the Tracker | 2026-02-23 | Done
1222 | 2026-02-23 | 9 | 56 | EmergencyStop | Emergency Released | 2026-02-23 | Done
1223 | 2026-02-23 | 20 | 93 | MotorOverCur | Replaced | 2026-02-24 | Done | Transmision shaft damage
1224 | 2026-02-23 | 31 | 40 | no communication | Reset the Tracker | 2026-02-23 | Done
1225 | 2026-02-23 | 49 | 49 | no communication | Reset the Tracker | 2026-02-23 | Done
1226 | 2026-02-23 | 55 | 56 | no communication | Reset the Tracker | 2026-02-23 | Done
1227 | 2026-02-23 | 55 | 102 | MotorOverCur | Reset the Tracker | 2026-02-23 | Done
1228 | 2026-02-23 | 59 | 45 | no communication | Reset the Tracker | 2026-02-23 | Done
1229 | 2026-02-23 | 80 | 99 | no communication | Reset the Tracker | 2026-02-23 | Done
1230 | 2026-02-23 | 80 | 100 | no communication | Reset the Tracker | 2026-02-23 | Done
1231 | 2026-02-23 | 80 | 125 | no communication | Reset the Tracker | 2026-02-23 | Done
1232 | 2026-02-23 | 81 | 36 | EmergencyStop | Replaced | 2026-02-25 | Done | Bearing Need to be Changed
1233 | 2026-02-23 | 91 | 34 | MotorOverCur | Replcaed | 2026-02-24 | Done | Gasket Missing
1234 | 2026-02-23 | 95 | 66 | no communication | Reset the Tracker | 2026-02-23 | Done
1235 | 2026-02-23 | 121 | 135 | MotorOverCur | Replcaed | 2026-02-24 | Done | Transmision shaft damage
1236 | 2026-02-24 | 22 | 44 | no communication | Reset the Tracker | 2026-02-24 | Done
1237 | 2026-02-24 | 39 | 105 | no communication | Reset the Tracker | 2026-02-24 | Done
1238 | 2026-02-24 | 64 | 10 | BatSOCLow | Reset the Tracker | 2026-02-24 | Done
1239 | 2026-02-24 | 126 | 95 | no communication | Reset the Tracker | 2026-02-24 | Done
1240 | 2026-02-24 | 131 | 68 | no communication | Reset the Tracker | 2026-02-24 | Done
1241 | 2026-02-25 | 23 | 16 | no communication | Reset the Tracker | 2026-02-25 | Done
1242 | 2026-02-25 | 35 | 90 | no communication | Reset the Tracker | 2026-02-25 | Done
1243 | 2026-02-25 | 50 | 85 | no communication | Reset the Tracker | 2026-02-25 | Done
1244 | 2026-02-25 | 55 | 140 | no communication | Reset the Tracker | 2026-02-25 | Done
1245 | 2026-02-25 | 58 | 42 | BatSOCLow | Reset the Tracker | 2026-02-25 | Done
1246 | 2026-02-25 | 67 | 67 | no communication | Reset the Tracker | 2026-02-25 | Done
1247 | 2026-02-25 | 69 | 5 | no communication | Reset the Tracker | 2026-02-25 | Done
1248 | 2026-02-25 | 72 | 105 | no communication | Reset the Tracker | 2026-02-25 | Done
1249 | 2026-02-25 | 74 | 42 | no communication | Reset the Tracker | 2026-02-25 | Done
1250 | 2026-02-25 | 74 | 110 | no communication | Reset the Tracker | 2026-02-25 | Done
1251 | 2026-02-25 | 79 | 56 | no communication | Reset the Tracker | 2026-02-25 | Done
1252 | 2026-02-25 | 94 | 77 | no communication | Reset the Tracker | 2026-02-25 | Done
1253 | 2026-02-25 | 99 | 115 | no communication | Reset the Tracker | 2026-02-25 | Done
1254 | 2026-02-25 | 102 | 4 | no communication | Reset the Tracker | 2026-02-25 | Done
1255 | 2026-02-25 | 109 | 25 | BatSOCLow | Reset the Tracker | 2026-02-25 | Done
1256 | 2026-02-25 | 109 | 96 | BatSOCLow | Reset the Tracker | 2026-02-25 | Done
1257 | 2026-02-27 | 16 | 137 | AngleNoChg | Reset the Tracker | 2026-02-27 | Done
1258 | 2026-02-27 | 49 | 56 | no communication | Reset the Tracker | 2026-02-27 | Done
1259 | 2026-02-27 | 55 | 116 | no communication | Reset the Tracker | 2026-02-27 | Done
1260 | 2026-02-27 | 75 | 41 | no communication | Reset the Tracker | 2026-02-27 | Done
1261 | 2026-02-27 | 86 | 17 | no communication | Reset the Tracker | 2026-02-27 | Done
1262 | 2026-02-27 | 89 | 139 | no communication | Reset the Tracker | 2026-02-27 | Done
1263 | 2026-02-27 | 103 | 34 | no communication | Reset the Tracker | 2026-02-27 | Done
1264 | 2026-02-27 | 109 | 118 | no communication | Reset the Tracker | 2026-02-27 | Done
1265 | 2026-02-27 | 114 | 120 | no communication | Reset the Tracker | 2026-02-27 | Done
1266 | 2026-02-27 | 130 | 32 | MotorOverCur | Replaced | 2026-02-28 | Done | Transmision shaft damage
1267 | 2026-02-28 | 14 | 4 | MotorOverCur | Replaced | 2026-03-01 | Done | Transmission shaft damage
1268 | 2026-02-28 | 42 | 52 | no communication | Reset the tracker | 2026-02-28 | Done
1269 | 2026-02-28 | 43 | 105 | no communication | Reset the tracker | 2026-02-28 | Done
1270 | 2026-02-28 | 60 | 91 | no communication | Reset the tracker | 2026-02-28 | Done
1271 | 2026-02-28 | 60 | 109 | MotorOverCur | Replaced | 2026-03-01 | Done | Bearing damage
1272 | 2026-02-28 | 70 | 63 | no communication | Reset the tracker | 2026-02-28 | Done
1273 | 2026-02-28 | 80 | 3 | BatSOCLow | Reset the tracker | 2026-02-28 | Done
1274 | 2026-02-28 | 82 | 53 | no communication | Reset the tracker | 2026-02-28 | Done
1275 | 2026-02-28 | 95 | 13 | no communication | Reset the tracker | 2026-02-28 | Done
1276 | 2026-02-28 | 95 | 101 | no communication | Reset the tracker | 2026-02-28 | Done
1277 | 2026-02-28 | 95 | 117 | no communication | Reset the tracker | 2026-02-28 | Done
1278 | 2026-02-28 | 123 | 61 | BatSOCLow | Reset the tracker | 2026-02-28 | Done
1279 | 2026-02-28 | 131 | 112 | MotorOverCur | Replaced | 2026-03-01 | Done | Transmission shaft damage
1280 | 2026-03-01 | 1 | 19 | BatSOCLow | Reset the Tracker | 2026-03-01 | Done
1281 | 2026-03-01 | 11 | 95 | EmergencyStop | Replaced | 2026-03-02 | Done | Bearing need to be Changed
1282 | 2026-03-01 | 25 | 69 | MotorOverCur | Reset the Tracker | 2026-03-01 | Done
1283 | 2026-03-01 | 39 | 105 | no communication | Reset the Tracker | 2026-03-01 | Done
1284 | 2026-03-01 | 60 | 109 | MotorOverCur |  |  | Pending | Drive fail
1285 | 2026-03-02 | 23 | 16 | no communication | Reset the Tracker | 2026-03-02 | Done
1286 | 2026-03-02 | 23 | 22 | no communication | Reset the Tracker | 2026-03-02 | Done
1287 | 2026-03-02 | 53 | 109 | AngleNoChg |  |  | Pending | Transmission shaft damaged
1288 | 2026-03-02 | 63 | 15 | no communication | Reset the Tracker | 2026-03-02 | Done
1289 | 2026-03-02 | 71 | 1 | no communication | Reset the Tracker | 2026-03-02 | Done
1290 | 2026-03-02 | 80 | 3 | BatSOCLow | Reset the Tracker | 2026-03-02 | Done
1291 | 2026-03-02 | 80 | 39 | BatSOCLow | Reset the Tracker | 2026-03-02 | Done
1292 | 2026-03-02 | 95 | 68 | BatSOCLow | Reset the Tracker | 2026-03-02 | Done
1293 | 2026-03-02 | 95 | 71 | no communication | Reset the Tracker | 2026-03-02 | Done
1294 | 2026-03-02 | 100 | 123 | no communication | Reset the Tracker | 2026-03-02 | Done
1295 | 2026-03-02 | 109 | 96 | BatSOCLow | Reset the Tracker | 2026-03-02 | Done
1296 | 2026-03-02 | 114 | 138 | no communication | Reset the Tracker | 2026-03-02 | Done
1297 | 2026-03-03 | 33 | 4 | no communication | Reset the Tracker | 2026-03-03 | Done
1298 | 2026-03-03 | 67 | 27 | no communication | Reset the Tracker | 2026-03-03 | Done
1299 | 2026-03-03 | 70 | 26 | no communication | Reset the Tracker | 2026-03-03 | Done
1300 | 2026-03-03 | 81 | 125 | no communication | Reset the Tracker | 2026-03-03 | Done
1301 | 2026-03-03 | 90 | 99 | no communication | Reset the Tracker | 2026-03-03 | Done
1302 | 2026-03-04 | 5 | 2 | no communication | Reset the Tracker | 2026-03-04 | Done
1303 | 2026-03-04 | 54 | 114 | AngleNoCom | Reset the Tracker | 2026-03-04 | Done
1304 | 2026-03-04 | 80 | 3 | no communication | Reset the Tracker | 2026-03-04 | Done
1305 | 2026-03-04 | 80 | 59 | no communication | Reset the Tracker | 2026-03-04 | Done
1306 | 2026-03-04 | 101 | 49 | BatSOCLow | Reset the Tracker | 2026-03-04 | Done
1307 | 2026-03-04 | 109 | 25 | BatSOCLow | Reset the Tracker | 2026-03-04 | Done
1308 | 2026-03-04 | 109 | 65 | no communication | Reset the Tracker | 2026-03-04 | Done
1309 | 2026-03-04 | 109 | 87 | BatSOCLow | Reset the Tracker | 2026-03-04 | Done
1310 | 2026-03-04 | 121 | 98 | MotorOverCur |  |  | Pending | Bearing Need to be Changed
1311 | 2026-03-04 | 95 | 68 | no communication | Reset the Tracker | 2026-03-04 | Done
1312 | 2026-03-05 | 22 | 17 | BatSOCLow | Reset the Tracker | 2026-03-05 | Done
1313 | 2026-03-05 | 30 | 128 | EmergencyStop |  |  | Pending | Transmission shaft damaged
1314 | 2026-03-05 | 45 | 9 | no communication | Reset the Tracker | 2026-03-05 | Done
1315 | 2026-03-05 | 74 | 49 | no communication | Reset the Tracker | 2026-03-05 | Done
1316 | 2026-03-05 | 65 | 109 | no communication | Reset the Tracker | 2026-03-05 | Done
1317 | 2026-03-05 | 114 | 24 | no communication | Reset the Tracker | 2026-03-05 | Done
1318 | 2026-03-05 | 95 | 58 | no communication | Reset the Tracker | 2026-03-05 | Done
1319 | 2026-03-06 | 18 | 85 | EmergencyStop | Emergency released | 2026-03-06 | Done
1320 | 2026-03-06 | 74 | 27 | no communication | Reset the Tracker | 2026-03-06 | Done
1321 | 2026-03-07 | 18 | 85 | EmergencyStop | Emergency Released | 2026-03-07 | Done
1322 | 2026-03-07 | 22 | 15 | no communication | Reset the Tracker | 2026-03-07 | Done
1323 | 2026-03-07 | 23 | 3 | MotorOverCur | Transmission shaft damaged |  | Pending | TRansmission shaft damaged
1325 | 2026-03-07 | 48 | 57 | MotorOverCur | Gasket Missing |  | Pending | Gasket Missing
1328 | 2026-03-07 | 74 | 27 | no communication | Reset the Tracker | 2026-03-07 | Done
1329 | 2026-03-07 | 94 | 128 | no communication | Reset the Tracker | 2026-03-07 | DOne
1330 | 2026-03-07 | 102 | 106 | no communication | Reset the Tracker | 2026-03-07 | Done
1333 | 2026-03-09 | 30 | 125 | no communication | Reset the Tracker | 2026-03-09 | Done
1338 | 2026-03-09 | 80 | 39 | no communication | Reset the Tracker | 2026-03-09 | Done
1339 | 2026-03-09 | 80 | 59 | no communication | Reset the Tracker | 2026-03-09 | Done
1340 | 2026-03-09 | 80 | 106 | no communication | Reset the Tracker | 2026-03-09 | Done
1341 | 2026-03-09 | 109 | 25 | no communication | Reset the Tracker | 2026-03-09 | Done
1342 | 2026-03-09 | 109 | 87 | no communication | Reset the Tracker | 2026-03-09 | Done
1344 | 2026-03-09 | 95 | 102 | no communication | Reset the Tracker | 2026-03-09 | Done
1345 | 2026-03-09 | 95 | 135 | no communication | Reset the Tracker | 2026-03-09 | Done
1346 | 2026-03-09 | 130 | 103 | MotorOverCur | Transmission shaft damaged | 2026-03-09 | Pending
1348 | 2026-03-10 | 23 | 54 | no communication | Reset the Tracker | 2026-03-10 | Done
1351 | 2026-03-10 | 35 | 55 | no communication | Reset Tracker | 2026-03-10 | Done
1354 | 2026-03-10 | 70 | 16 | no communication | Reset the Tracker | 2026-03-10 | Done
1355 | 2026-03-10 | 80 | 81 | no communication | Reset the Tracker | 2026-03-10 | Done
1356 | 2026-03-10 | 81 | 109 | no communication | Reset the Tracker | 2026-03-10 | Done
1357 | 2026-03-10 | 87 | 94 | no communication | Reset the Tracker | 2026-03-10 | Done
1358 | 2026-03-10 | 94 | 31 | no communication | Reset the Tracker | 2026-03-10 | Done
1359 | 2026-03-10 | 94 | 138 | MotorOverCur | Transmission Shaft damaged | 2026-03-10 | Pending
1360 | 2026-03-10 | 109 | 24 | no communication | Reset the Tracker | 2026-03-10 | Done
1362 | 2026-03-10 | 123 | 3 | EmergencyStop | Reset the Tracker | 2026-03-10 | Done
1363 | 2026-03-10 | 123 | 71 | no communication | Reset the Tracker | 2026-03-10 | Done
1364 | 2026-03-11 | 17 | 65 | EmergencyStop | Emergency Released | 2026-03-11 | Done
1365 | 2026-03-11 | 17 | 68 | EmergencyStop | Emergency Released | 2026-03-11 | Done
1366 | 2026-03-11 | 19 | 32 | AngleNoChg | Reset the Tracker | 2026-03-11 | Done
1367 | 2026-03-11 | 55 | 53 | BatSOCLow | Reset the Tracker | 2026-03-11 | Done
1368 | 2026-03-11 | 81 | 83 | BatSOCLow | Reset the Tracker | 2026-03-11 | Done
1369 | 2026-03-11 | 100 | 123 | no communication | Reset the Tracker | 2026-03-11 | Done

## Inverter and MVPS
Total |  |  | 286
Rectified |  |  | 298
Pending |  |  | -12
S. No | Date | Block No | Module No | Inverter No | Issue | Action Taken | Rectification date | Status | Remarks
1 | 2025-08-28 | 15 | 7 | 2 | GFDI ground fault | 1. SCB-32, Sting-11, MC4 melt 2. Fuse replced and rectified the fault | 2025-08-28 | Done
2 | 2025-08-25 | 51 | 2 | 1 | GFDI ground fault | 1. Stop due to GFDI at SCB-3 2. Fuse replced and rectified the fault | 2025-08-25 | Done
3 | 2025-08-25 | 76 | 8 | 2 | GFDI ground fault | 1. Stop due to GFDI at SCB-31 2. Fuse replced and rectified the fault | 2025-08-25 | Done
4 | 2025-08-31 | 80 | 8 | 2 | GFDI ground fault | 1. Power settting 2. Fuse replced and rectified the fault | 2025-08-31 | Done
5 | 2025-08-31 | 109 | 8 | 2 | GFDI ground fault | 1. Stop due to GFDI at inv-6 2. Fuse replced and rectified the fault | 2025-08-31 | Done
6 | 2025-08-31 | 121 | 5,6,7,8 | 2 | Stop state, Not working | 1. Reset the Inverter and running | 2025-08-31 | Done
7 | 2025-08-25 | 125 | 8 | 2 | GFDI ground fault | 1. Stop due to GFDI at SCB-28 2. Fuse replced and rectified the fault | 2025-08-25 | Done
8 | 2025-08-25 | 15 | 5,6,7,8 | 2 | GFDI ground fault | 1. SCB-32, Sting-11, MC4 melt 2. Fuse replced and rectified the fault | 2025-08-25 | Done
9 | 2025-08-25 | 109 | 6 | 2 | GFDI ground fault | 1. Stop due to GFDI at inv-6 2. Fuse replced and rectified the fault | 2025-08-25 | Done
10 | 2025-09-01 | 121 | 8 | 2 | Control supply fault | 1. PW board replaced | 2025-09-01 | Done
11 | 2025-09-02 | 46 | 7 | 2 | DC switch 1, NOT Working | 1. IGBT driver board replaced | 2025-09-02 | Done
12 | 2025-09-06 | 109 |  | 2 | Communication Issue | No fault found. Reset Board | 2025-09-06 | Done
13 | 2025-09-05 | 21 | 6 | 2 | Reactor Over Temperature |  | 2025-09-05 | Done
14 | 2025-09-14 | 52 | 3 | 1 | GFDI ground fault | No fault found. Reset Board | 2025-09-14 | Done
15 | 2025-09-14 | 64 | 3 | 1 | GFDI ground fault | Fuse and resistor replaced | 2025-09-14 | Done
16 | 2025-09-14 | 25 | 1 | 1 | GFDI ground fault | Resistor Replaced | 2025-09-14 | Done
17 | 2025-09-15 | 102 | 2,3,4 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-15 | Done
18 | 2025-09-14 | 102 | 1 | 1 | GFDI ground fault | AC Side fuse cable changed | 2025-09-14 | Done
19 | 2025-09-14 | 126 | 8 | 2 | GFDI ground fault | No fault found. Reset Board | 2025-09-14 | Done
20 | 2025-09-16 | 38 | 5 | 2 | Sync Fault | Rebot inverter | 2025-09-16 | Done
21 | 2025-09-20 | 118 | 3 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-20 | Done
22 | 2025-09-20 | 118 | 5 | 2 | Access Control protection | No fault found. Reset Board | 2025-09-20 | Done
23 | 2025-09-21 | 125 | 6 | 2 | GFDI ground fault | SCB replaced. Fuse and Resistor Replaced | 2025-09-21 | Done
24 | 2025-09-21 | 48 | 8 | 2 | GFDI ground fault | No fault found. Reset Board | 2025-09-21 | Done
25 | 2025-09-21 | 52 | 4 | 1 | Low Insulation resistance | No fault found. Reset Board | 2025-09-21 | Done
26 | 2025-09-22 | 25 | 4 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-22 | Done
27 | 2025-09-22 | 90 | 1 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-22 | Done
28 | 2025-09-22 | 98 | 2 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-22 | Done
29 | 2025-09-22 | 102 | 3,4,5 | 1 | Communication Issue | No fault found. Reset Board | 2025-09-22 | Done
30 | 2025-09-23 | 90 | 6 | 2 | Access Control protection | No fault found. Reset Board | 2025-09-23 | Done
31 | 2025-09-23 | 52 | 4 | 1 | GFDI ground fault | No fault found. Reset Board | 2025-09-23 | Done
32 | 2025-09-24 | 52 | 4 | 1 | GFDI ground fault | No fault found. Reset Board | 2025-09-24 | Done
33 | 2025-09-24 | 56 | 4 | 1 | Access Control protection | No fault found. Reset Board | 2025-09-24 | Done
34 | 2025-09-24 | 80 | 5 | 2 | Sync Fault | Rebot inverter | 2025-09-24 | Done
35 | 2025-09-24 | 102 | 2,3,4 | 1 | Communication Issue | No fault found. Reset Board | 2025-09-24 | Done
36 | 2025-09-25 | 48 | 8 | 2 | GFDI ground fault | No fault found. Fuse Replaced | 2025-09-25 | Done
37 | 2025-09-27 | 40 | 2,3,4 | 1 | Parallel Machine Communication Fault | PE board Replaced | 2025-09-27 | Done
38 | 2025-09-27 | 65 | 5 | 2 | GFDI ground fault | String 1 SCB 13 MC4 Melt. Fuse also replaced. Rectified | 2025-09-27 | Done
39 | 2025-09-27 | 121 | 5,6,7,8 | 2 | Control supply abnormal | Tighten PW1 board cables | 2025-09-27 | Done
40 | 2025-09-27 | 114 | 6 | 2 | AC Current Imbalance | No fault found. Reset Board | 2025-09-27 | Done
41 | 2025-09-27 | 91 | 5 | 2 | Access Control protection | No fault found. Reset Board | 2025-09-27 | Done
42 | 2025-09-27 | 73 |  |  | WT show high temperature | Adjust Winding Temperature Indicator | 2025-09-27 | Done
43 | 2025-09-28 | 121 | 5,6,7,8 | 2 | Control supply abnormal | PD Board Replaced | 2025-09-28 | Done
44 | 2025-09-29 | 121 | 5,6,7,8 | 2 | Control supply abnormal | SCU Board Wiring tightness | 2025-09-29 | Done
45 | 2025-09-29 | 60 |  | 1 | Device connection issue | Cable lug termination rectify | 2025-09-29 | Done
46 | 2025-09-29 | 83 |  |  | Communication Issue | ETAP Controller Changed | 2025-09-29 | Done
47 | 2025-09-30 | 121 | 5,6,7,8 | 2 | Control supply abnormal | SCU Board Software Update | 2025-09-30 | Done
48 | 2025-09-30 | 75 |  |  | Communication Issue | Power Cable Tighten | 2025-09-30 | Done
49 | 2025-10-01 | 121 | 5,6,7,8 | 2 | Control supply abnormal | SCU Board Replaced | 2025-10-01 | Done
50 | 2025-10-01 | 113 |  |  | Communication Issue | Communication Power Cable Tighten | 2025-10-01 | Done
51 | 2025-10-02 | 102 | 2,3,4 | 1 | IO-DSP Supply Issue | Rebot inverter | 2025-10-02 | Done
52 | 2025-10-04 | 114 |  | 1 | Off Grid | Due to Communication Issue | 2025-10-04 | Done
53 | 2025-10-06 | 22 | 1 | 1 | Access Control protection | Rebot inverter | 2025-10-06 | Done
54 | 2025-10-06 | 34 | 5 | 2 | Access Control protection | Rebot inverter | 2025-10-06 | Done
55 | 2025-10-06 | 75 |  | 1 | IO Board Communication Error | Wiring termination changed at UPS Side | 2025-10-06 | Done
56 | 2025-10-06 | 76 |  | 1 | IO Board Communication Error | Termination Crimping rectified | 2025-10-06 | Done
57 | 2025-10-06 | 31 |  | 1 | Abnormal derating of axial fan flow | Fan 4 Replaced | 2025-10-06 | Done
58 | 2025-10-07 | 54 | 2,4 | 1 | Access Control protection | Rebot inverter | 2025-10-07 | Done
59 | 2025-10-07 | 54 | 7 | 2 | Access Control protection | Rebot inverter | 2025-10-07 | Done
60 | 2025-10-07 | 131 |  |  | Off Grid | Due to Communication Issue | 2025-10-07 | Done
61 | 2025-10-07 | 109 |  |  | Off Grid | Due to Communication Issue | 2025-10-07 | Done
62 | 2025-10-07 | 79 |  |  | Off Grid | Due to Communication Issue | 2025-10-07 | Done
63 | 2025-10-07 | 14 | 1 | 1 | Low Insulation resistance | No issue found. Reset Inverter | 2025-10-07 | Done
64 | 2025-10-08 | 132 |  |  | Off Grid | Due to Communication Issue | 2025-10-08 | Done
65 | 2025-10-08 | 63 |  |  | PMD IO Board Comm Error | Cable tightness done at UPS end | 2025-10-08 | Done
66 | 2025-10-10 | 130 | 2 | 1 | Shutdown | Rebot inverter | 2025-10-10 | Done
67 | 2025-10-12 | 117 | 6 | 2 | Low Insulation resistance | Cable replaced near AI box | 2025-10-12 | Done
68 | 2025-10-12 | 2 | 7,8 | 2 | Access Control protection | Rebot inverter | 2025-10-12 | Done
69 | 2025-10-13 | 11 | 8 | 2 | Low Insulation resistance | SCB 33 String 16 faulty. Rectified | 2025-10-13 | Done
70 | 2025-10-14 | 42 | 1 | 1 | Shutdown | Rebot inverter | 2025-10-14 | Done
71 | 2025-10-17 | 62 |  | 1 | Shutdown | Rebot inverter | 2025-10-17 | Done
72 | 2025-10-18 | 114 | 4 | 1 | Standby | DC Breaker switch in manual mode | 2025-10-18 | Done
73 | 2025-10-18 | 76 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-18 | Done
74 | 2025-10-18 | 72 | 2 | 1 | Emergency Stop | Rebot inverter | 2025-10-18 | Done
75 | 2025-10-19 | 84 | 5 | 2 | Emergency Stop | Rebot inverter | 2025-10-19 | Done
76 | 2025-10-19 | 72 | 2 | 1 | Emergency Stop | Rebot inverter | 2025-10-19 | Done
77 | 2025-10-20 | 30 | 5 | 2 | Access Control protection | Rebot inverter | 2025-10-20 | Done
78 | 2025-10-20 | 110 | 7,8 | 2 | Shutdown | Rebot inverter | 2025-10-20 | Done
79 | 2025-10-20 | 125 | 4 | 1 | Emergency Stop | Rebot inverter | 2025-10-20 | Done
80 | 2025-10-20 | 125 | 6,8 | 2 | Shutdown | Rebot inverter | 2025-10-20 | Done
81 | 2025-10-21 | 3 | 8 | 2 | Shutdown | Rebot inverter | 2025-10-21 | Done
82 | 2025-10-21 | 1 | 5,6,7,8 | 2 | Emergency Stop | Rebot inverter | 2025-10-21 | Done
83 | 2025-10-22 | 2 | 2,3 | 1 | Emergency Stop | Rebot inverter | 2025-10-22 | Done
84 | 2025-10-23 | 127 | 6,5,4, | 2 | DC OVER current | Reset | 2025-10-23 | Done
85 | 2025-10-23 | 132 | 6 | 2 | GFDI ground fault | 1A Fuse replaced | 2025-10-23 | Done
86 | 2025-10-27 | 77 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-27 | Done
87 | 2025-10-29 | 121 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-29 | Done
88 | 2025-10-30 | 92 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-30 | Done
89 | 2025-11-02 | 126 |  |  | DAS reset | Reset | 2025-11-02 | Done
90 | 2025-11-04 | 51 | 6 | 2 | Access Control protection | Rebot inverter | 2025-11-04 | Done
91 | 2025-11-04 | 126 |  |  | Communication Interphase issue | Replaced new Interphase | 2025-11-04 | Done
92 | 2025-11-05 | 48 | 2 | 1 | DC Overvoltage | Reset | 2025-11-05 | Done
93 | 2025-11-05 | 48 | 8 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
94 | 2025-11-05 | 71 | 5 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
95 | 2025-11-05 | 49 | 8 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
96 | 2025-11-05 | 61 | 6 | 1 | DC Overvoltage | Reset | 2025-11-05 | Done
97 | 2025-11-05 | 61 | 7 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
98 | 2025-11-05 | 109 | 5 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
99 | 2025-11-05 | 92 |  |  | Emergency Stop | Reset | 2025-11-05 | Done
100 | 2025-11-07 | 131 | 4 | 1 | DC Overvoltage | Reset | 2025-11-07 | Done
101 | 2025-11-07 | 112 | 7 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
102 | 2025-11-07 | 99 | 6 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
103 | 2025-11-07 | 74 | 6 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
104 | 2025-11-07 | 94 | 7 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
105 | 2025-11-07 | 108 | 1 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
106 | 2025-11-07 | 123 | 8 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
107 | 2025-11-07 | 70 | 7 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
108 | 2025-11-07 | 94 | 2 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
109 | 2025-11-07 | 23 | 8 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
110 | 2025-11-07 | 33 | 3 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
111 | 2025-11-07 | 18 | 6 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
112 | 2025-11-07 | 54 |  |  | Off Grid |  | 2025-11-07 | Done
113 | 2025-11-09 | 8 | 3 | 1 | Initial Standby | Reset | 2025-11-09 | Done
114 | 2025-11-09 | 15 | 1 | 6 | Access Control protection | Reset | 2025-11-09 | Done
115 | 2025-11-09 | 129 | 1 | 6 | Initial Standby | Reset | 2025-11-09 | Done
116 | 2025-11-10 | 15 | 1 | 1 | Access Control protection | Reset | 2025-11-10 | Done
117 | 2025-11-10 | 54 | 7 | 2 | Access Control protection | Reset | 2025-11-10 | Done
118 | 2025-11-10 | 108 | 7 | 2 | DC Overvoltage | Reset | 2025-11-10 | Done
119 | 2025-11-10 | 108 | 2,3,4 | 1 | DC Overvoltage | Reset | 2025-11-10 | Done
120 | 2025-11-12 | 78 | 6 | 2 | Access Control protection | Reset | 2025-11-12 | Done
121 | 2025-11-12 | 104 | 4 | 1 | Access Control protection | Reset | 2025-11-12 | Done
122 | 2025-11-14 | 15 | 1 | 1 | Shutdown | Reset | 2025-11-14 | Done
123 | 2025-11-14 | 67 | 6 | 2 | Shutdown | Reset | 2025-11-14 | Done
124 | 2025-11-14 | 67 | 8 | 2 | Shutdown | Reset | 2025-11-14 | Done
125 | 2025-11-14 | 90 | 1 | 1 | Shutdown | Reset | 2025-11-14 | Done
126 | 2025-11-14 | 90 | 4 | 1 | Shutdown | Reset | 2025-11-14 | Done
127 | 2025-11-14 | 90 | 5 | 2 | Shutdown | Reset | 2025-11-14 | Done
128 | 2025-11-14 | 90 | 8 | 2 | Shutdown | Reset | 2025-11-14 | Done
129 | 2025-11-15 | 19 | 5 | 2 | GFDI | Reset | 2025-11-15 | Done
130 | 2025-11-15 | 28 | 4 | 1 | GFDI | Reset | 2025-11-15 | Done
131 | 2025-11-15 | 125 | 6 | 2 | GFDI | Reset | 2025-11-15 | Done
132 | 2025-11-15 | 92 | 6 | 2 | DC Overvoltage | Reset | 2025-11-15 | Done
133 | 2025-11-15 | 73 |  | 2 | DC Overvoltage | Reset | 2025-11-15 | Done
134 | 2025-11-15 | 41 |  | 1 | DC Overvoltage | Reset | 2025-11-15 | Done
135 | 2025-11-15 | 105 | 7 | 2 | AC Current Imbalance | Reset | 2025-11-15 | Done
136 | 2025-10-17 | 62 |  | 1 | Shutdown | Rebot inverter | 2025-10-18 | Done
137 | 2025-10-18 | 114 | 4 | 1 | Standby | DC Breaker switch in manual mode | 2025-10-18 | Done
138 | 2025-10-18 | 76 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-18 | Done
139 | 2025-10-18 | 72 | 2 | 1 | Emergency Stop | Rebot inverter | 2025-10-18 | Done
140 | 2025-10-19 | 84 | 5 | 2 | Emergency Stop | Rebot inverter | 2025-10-19 | Done
141 | 2025-10-19 | 72 | 2 | 1 | Emergency Stop | Rebot inverter | 2025-10-19 | Done
142 | 2025-10-20 | 30 | 5 | 2 | Access Control protection | Rebot inverter | 2025-10-20 | Done
143 | 2025-10-20 | 110 | 7,8 | 2 | Shutdown | Rebot inverter | 2025-10-20 | Done
144 | 2025-10-20 | 125 | 4 | 1 | Emergency Stop | Rebot inverter | 2025-10-20 | Done
145 | 2025-10-20 | 125 | 6,8 | 2 | Shutdown | Rebot inverter | 2025-10-20 | Done
146 | 2025-10-21 | 3 | 8 | 2 | Shutdown | Rebot inverter | 2025-10-21 | Done
147 | 2025-10-21 | 1 | 5,6,7,8 | 2 | Emergency Stop | Rebot inverter | 2025-10-21 | Done
148 | 2025-10-22 | 2 | 2,3 | 1 | Emergency Stop | Rebot inverter | 2025-10-22 | Done
149 | 2025-10-23 | 127 | 6,5,4, | 2 | DC OVER current | Reset | 2025-10-23 | Done
150 | 2025-10-23 | 132 | 6 | 2 | GFDI ground fault | 1A Fuse replaced | 2025-10-23 | Done
151 | 2025-10-27 | 77 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-10-30 | Done
152 | 2025-10-29 | 121 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-11-04 | Done
153 | 2025-10-30 | 92 |  |  | Off Grid | Off grid inverter due to loop 3 communication | 2025-11-04 | Done
154 | 2025-11-02 | 126 |  |  | DAS reset | Reset | 2025-11-02 | Done
155 | 2025-11-04 | 51 | 6 | 2 | Access Control protection | Rebot inverter | 2025-11-04 | Done
156 | 2025-11-04 | 126 |  |  | Communication Interphase issue | Replaced new Interphase | 2025-11-06 | Done
157 | 2025-11-05 | 48 | 2 | 1 | DC Overvoltage | Reset | 2025-11-05 | Done
158 | 2025-11-05 | 48 | 8 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
159 | 2025-11-05 | 71 | 5 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
160 | 2025-11-05 | 49 | 8 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
161 | 2025-11-05 | 61 | 6 | 1 | DC Overvoltage | Reset | 2025-11-05 | Done
162 | 2025-11-05 | 61 | 7 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
163 | 2025-11-05 | 109 | 5 | 2 | DC Overvoltage | Reset | 2025-11-05 | Done
164 | 2025-11-05 | 92 |  |  | Emergency Stop | Reset | 2025-11-05 | Done
165 | 2025-11-07 | 131 | 4 | 1 | DC Overvoltage | Reset | 2025-11-07 | Done
166 | 2025-11-07 | 112 | 7 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
167 | 2025-11-07 | 99 | 6 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
168 | 2025-11-07 | 74 | 6 | 2 | Emergency Stop | Reset | 2025-11-07 | Done
169 | 2025-11-07 | 94 | 7 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
170 | 2025-11-07 | 108 | 1 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
171 | 2025-11-07 | 123 | 8 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
172 | 2025-11-07 | 70 | 7 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
173 | 2025-11-07 | 94 | 2 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
174 | 2025-11-07 | 23 | 8 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
175 | 2025-11-07 | 33 | 3 | 1 | AC overvoltage | Reset | 2025-11-07 | Done
176 | 2025-11-07 | 18 | 6 | 2 | AC overvoltage | Reset | 2025-11-07 | Done
177 | 2025-11-07 | 54 |  |  | Off Grid |  | 2025-11-08 | Done
178 | 2025-11-09 | 8 | 3 | 1 | Initial Standby | Reset | 2025-11-09 | Done
179 | 2025-11-09 | 15 | 1 | 6 | Access Control protection | Reset | 2025-11-09 | Done
180 | 2025-11-09 | 129 | 1 | 6 | Initial Standby | Reset | 2025-11-09 | Done
181 | 2025-11-10 | 15 | 1 | 1 | Access Control protection | Reset | 2025-11-10 | Done
182 | 2025-11-10 | 54 | 7 | 2 | Access Control protection | Reset | 2025-11-10 | Done
183 | 2025-11-10 | 108 | 7 | 2 | DC Overvoltage | Reset | 2025-11-10 | Done
184 | 2025-11-10 | 108 | 2,3,4 | 1 | DC Overvoltage | Reset | 2025-11-10 | Done
185 | 2025-11-12 | 78 | 6 | 2 | Access Control protection | Reset | 2025-11-12 | Done
186 | 2025-11-12 | 104 | 4 | 1 | Access Control protection | Reset | 2025-11-12 | Done
187 | 2025-11-14 | 15 | 1 | 1 | Shutdown | Reset | 2025-11-14 | Done
188 | 2025-11-14 | 67 | 6 | 2 | Shutdown | Reset | 2025-11-14 | Done
189 | 2025-11-14 | 67 | 8 | 2 | Shutdown | Reset | 2025-11-14 | Done
190 | 2025-11-14 | 90 | 1 | 1 | Shutdown | Reset | 2025-11-14 | Done
191 | 2025-11-14 | 90 | 4 | 1 | Shutdown | Reset | 2025-11-14 | Done
192 | 2025-11-14 | 90 | 5 | 2 | Shutdown | Reset | 2025-11-14 | Done
193 | 2025-11-14 | 90 | 8 | 2 | Shutdown | Reset | 2025-11-14 | Done
194 | 2025-11-15 | 19 | 5 | 2 | GFDI | SCB 10 ISOLATED | 2025-11-17 | Done
195 | 2025-11-15 | 28 | 4 | 1 | GFDI | SCB 4 ISOLATED | 2025-11-17 | Done
196 | 2025-11-15 | 125 | 6 | 2 | GFDI | SCB 6 ISOLATED | 2025-11-17 | Done
197 | 2025-11-15 | 92 | 6 | 2 | DC Overvoltage | Reset | 2025-11-15 | Done
198 | 2025-11-15 | 73 |  | 2 | DC Overvoltage | Reset | 2025-11-15 | Done
199 | 2025-11-15 | 41 |  | 1 | DC Overvoltage | Reset | 2025-11-15 | Done
200 | 2025-11-15 | 105 | 7 | 2 | AC Current Imbalance | Reset | 2025-11-15 | Done
201 | 2025-11-17 | 8 | 6 | 2 | GFDI | SCB 6 ISOLATED | 2025-11-17 | Done
202 | 2025-11-18 | 130 | ALL | BOTH | VCB INTERLOCKING | rectified Earthing interlock | 2025-11-18 | Done
203 | 2025-11-18 | 105 | 7 | 2 | Low Insulation resistance | RESET | 2025-11-18 | Done
204 | 2025-11-18 | 97 |  |  | LOOP 7 COMMUNICATION | OFFGRID | 2025-11-19 | Done
205 | 2025-11-19 | 128 | 2 | 1 | Low Insulation resistance | RESET | 2025-11-19 | Done
206 | 2025-11-20 | 4 | 2 | 1 | Low Insulation resistance | RESET | 2025-11-20 | Done
207 | 2025-11-20 | 113 | 2 | 1 | Low Insulation resistance | RESET | 2025-11-20 | Done
208 | 2025-11-20 | 11 | 7 | 2 | Low Insulation resistance | RESET | 2025-11-20 | Done
209 | 2025-11-21 | 117 | 3 | 1 | DC Overvoltage | RESET | 2025-11-21 | Done
210 | 2025-11-21 | 30 | 1 | 1 | Low Insulation resistance | RESET | 2025-11-21 | Done
211 | 2025-11-21 | 43 | 1 | 1 | Low Insulation resistance | RESET | 2025-11-21 | Done
212 | 2025-11-21 | 55 |  |  | idle | UPS TURNED ON | 2025-11-21 | Done
213 | 2025-11-21 | 56 |  |  | idle | UPS TURNED ON | 2025-11-21 | Done
214 | 2025-11-22 | 3 |  |  | Low Insulation resistance | RESET | 2025-11-22 | Done
215 | 2025-11-22 | 52 |  |  | Low Insulation resistance | RESET | 2025-11-22 | Done
216 | 2025-11-22 | 11 | 7 | 2 | Low Insulation resistance | RESET | 2025-11-22 | Done
217 | 2025-11-23 | 59 | 2 | 1 | Emergency Stop | RESET | 2025-11-23 | Done
218 | 2025-11-23 | 95 | 1 | 1 | Emergency Stop | RESET | 2025-11-23 | Done
219 | 2025-11-23 | 130 | 2 | 1 | DC OV | RESET | 2025-11-23 | Done
220 | 2025-11-23 | 126 | 3 | 1 | DC OV | RESET | 2025-11-23 | Done
221 | 2025-11-23 | 111 | 6 | 2 | DC OV | RESET | 2025-11-23 | Done
222 | 2025-11-23 | 24 | 7 | 2 | DC OV | RESET | 2025-11-23 | Done
223 | 2025-11-23 | 8 | 3 | 1 | DC OV | RESET | 2025-11-23 | Done
224 | 2025-11-23 | 77 | 3 | 1 | DC OV | RESET | 2025-11-23 | Done
225 | 2025-11-23 | 77 | 7 | 2 | DC OV | RESET | 2025-11-23 | Done
226 | 2025-11-23 | 77 | 8 | 2 | DC OV | RESET | 2025-11-23 | Done
227 | 2025-11-23 | 83 | 2 | 1 | DC OV | RESET | 2025-11-23 | Done
228 | 2025-11-23 | 83 | 6 | 2 | DC OV | RESET | 2025-11-23 | Done
229 | 2025-11-23 | 83 | 7 | 2 | DC OV | RESET | 2025-11-23 | Done
230 | 2025-11-24 | 77 | 7 | 2 | QS2 OFF | RESET | 2025-11-24 | Done
231 | 2025-11-24 | 62 | ALL | BOTH | STARTUP DELAY | RESET | 2025-11-24 | Done
232 | 2025-11-24 | 72 | ALL | BOTH | STARTUP DELAY | RESET | 2025-11-24 | Done
233 | 2025-11-24 | 72 | ALL | 2 | QS2 OFF | RESET | 2025-11-24 | Done
234 | 2025-11-24 | 35 | ALL | BOTH | ENERGIZATION DELAY | UPS RESTART TO UPDATE DS STATUS | 2025-11-24 | Done
235 | 2025-11-24 | 28 | ALL | BOTH | ENERGIZATION DELAY | UPS RESTART TO UPDATE DS STATUS | 2025-11-24 | Done
236 | 2025-11-25 | 43 | 4 | BOTH | DC OV | RESET | 2025-11-25 | Done
237 | 2025-11-26 | 121 | 7,3,4 | BOTH | DC OV | RESET | 2025-11-26 | Done
238 | 2025-11-26 | 124 | 2,3,7,8 | BOTH | DC OV | RESET | 2025-11-26 | Done
239 | 2025-11-26 | 120 | 6 | 2 | GFDI | SCB 17 ISOLATED , TRACKER 33 DAMAGED | 2025-11-26 | Done
240 | 2025-11-26 | 11 | 8 | 2 | Low Insulation resistance | RESET | 2025-11-26 | Done
241 | 2025-11-26 | 113 | 7 | 2 | Low Insulation resistance | RESET | 2025-11-26 | Done
242 | 2025-11-27 | 109 | ALL | BOTH | UPS DRAIN | RESET | 2025-11-27 | Done
243 | 2025-11-27 | 11 | 7 | 2 | Low Insulation resistance | SCB 33 String 16 faulty. Rectified | 2025-11-27 | Done
244 | 2025-11-28 | 77 | ALL | 1 | STARTUP DELAY | PD card CHANGED | 2025-12-06 | Done
245 | 2025-11-28 | 105 | ALL | 1 | STARTUP DELAY | RESET | 2025-11-28 | Done
246 | 2025-11-28 | 109 | ALL | BOTH | UPS DRAIN | RESET | 2025-11-28 | Done
247 | 2025-11-29 | 52 | 4 | 1 | Low Insulation resistance | SCB 23 STRING 5 ISOLATED | 2025-11-29 | Done
248 | 2025-12-01 | 105 | 7 | 2 | GFDI fault | Faulty string rectified | 2025-12-01 | Done
249 | 2025-12-08 | 125 | 6 | 2 | GFDI fault | SCB 23 STRING 5 ISOLATED | 2025-12-08 | Done
250 | 2025-12-10 | BAY 1 | ALL | ALL | DC OV | RESET | 2025-12-10 | Done
251 | 2025-12-11 | BAY 3 | ALL | ALL | DC OV | RESET | 2025-12-11 | Done
252 | 2025-12-11 | 108 | 1 | 2 | GFDI | RESET | 2025-12-11 | Done
253 | 2025-12-11 | 121 | 2 | ALL | GFDI | SCB 15 STRING 06 ISOLATED | 2025-12-11 | Done
254 | 2025-12-12 | 108 | 1 | 2 | GFDI | SCB 23 STRING 1 ISOLATED | 2025-12-12 | Done
255 | 2025-12-12 | 8 | 2 | ALL | 24h Insulation fault | RESET | 2025-12-12 | Done
256 | 2025-12-12 | 20 | ALL | ALL | 24h Insulation fault | RESET | 2025-12-12 | Done
257 | 2025-12-12 | 24 | 1 | ALL | 24h Insulation fault | RESET | 2025-12-12 | Done
258 | 2025-12-12 | 28 | ALL | ALL | DC OV | RESET | 2025-12-12 | Done
259 | 2025-12-12 | 35 | ALL | ALL | DC OV | RESET | 2025-12-12 | Done
260 | 2025-12-15 | 56 | 1 | 1 | Low Insulation resistance | SCB08 String 13-16 | 2025-12-15 | Done
261 | 2025-12-16 | 108 | 1 | 2 | GFDI | SCB03 SCB 23 STRING 1 ISOLATED | 2025-12-16 | Done
262 | 2025-12-17 | 35 | All | 2 | AC Under voltage | Reset the Inverter | 2025-12-17 | Done
263 | 2025-12-20 | 117 | 1 | 1 | 24H insulation | SCB 08 Strings 04 isolated - Red wire | 2025-12-22 | Done
264 | 2025-12-28 | 78 | 6 | 2 | GFDI | SCB16 String 11 | 2025-12-28 | Done
265 | 2026-01-04 | 7 | 4 | 1 | Low Insulation resistance | Auto reset | 2026-01-04 | Done
266 | 2026-01-05 | 7 | 4 | 1 | Low Insulation resistance | scb 10, String 3 Isolated | 2026-01-05 | Done
267 | 2026-01-05 | 127 | 3,4,5,6,7,8 | ALL | Ac switch Disconnection Fault | rectified using Castle Key | 2026-01-05 | Done
268 | 2026-01-05 | 56 | 2 | 1 | Low Insulation resistance | SCB 19 string 13, 14, 15, 16 are isolated | 2026-01-05 | Done
269 | 2026-01-16 | 116 | ALL | ALL | Press to shutdown | Change active power setting and give Rebot command | 2026-01-16 | Done
270 | 2026-01-18 | 117 | 3 | 1 | module Fault. IGBT Board faulty | Replaced with new module | 2026-01-20 | Done
271 | 2026-01-21 | 64 |  | 1 | Access Control protection | Reset | 2026-01-21 | Done
272 | 2026-01-21 | 64 |  | 2 | Access Control protection | Reset | 2026-01-21 | Done
273 | 2026-01-21 | 131 | 5 | 2 | Access Control protection | Reset | 2026-01-21 | Done
274 | 2026-01-21 | 131 | 7,8 | 2 | Access Control protection | Reset | 2026-01-21 | Done
275 | 2026-01-26 | 88 | 7 | 2 | Emergency Stop | Emergency Released | 2026-01-26 | Done
276 | 2026-01-30 | 34 | 6 | 2 | 24h Insulation fault | DCB 14 String 1 isolated. Inverter Reset | 2026-01-30 | Done
277 | 2026-02-02 | 13 | 1 | 1 | Module Fault | Drive board replaced | 2026-02-02 | Done
278 | 2026-02-06 | 108 | 2 | 1 | GFDI Fault | SCB 3 String 1 isolated. Resistor replaced | 2026-02-06 | Done
279 | 2026-02-16 | 87 | 1 | 1 | AC Under voltage | Reset the Inverter | 2026-02-16 | Done
280 | 2026-02-20 | 62 | 1 | 2 | Module Fault | IGBT Replaced | 2026-02-21 | Done
281 | 2026-02-25 | 99 | 2 | 1 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
282 | 2026-02-25 | 87 | 1 | 1 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
283 | 2026-02-25 | 87 | 2 | 1 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
284 | 2026-02-25 | 87 | 5 | 2 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
285 | 2026-02-25 | 87 | 7 | 2 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
286 | 2026-02-25 | 87 | 8 | 2 | DC over voltage | Reset the Inverter | 2026-02-25 | Done
287 | 2026-03-01 07:07 | 59 | 2,3,4 | INV-01 | Parallel machine communication fault | The O&M team performed a hard reset, and the module came back online. | 2026-03-01 08:17 | Done
288 | 2026-03-01 08:53 | 5 | 1 | INV-01 | DC Overvoltage | The O&M team performed a hard reset, and the module came back online. | 2026-03-01 09:31 | Done
289 | 2026-03-03 06:48 | 2 | INV-01 | INV-01 | Control Power Supply abnormal | The O&M team performed a hard reset, and the module came back online. | 2026-03-03 07:10 | Done
290 | 2026-03-05 06:48 | 2 | INV-01 | INV-01 | Control Power Supply abnormal | The O&M team performed a hard reset, and the module came back online. | 2026-03-05 07:10 | Done
291 | 2026-03-05 07:21 | 87 | Block | INV01 & INV02 | DC overvoltage | The O&M team performed a hard reset, and the module came back online. | 2026-03-05 09:33 | Done
292 | 2026-03-05 07:23 | 99 | INV-01 | INV-01 | DC overvoltage | The O&M team performed a hard reset, and the module came back online. | 2026-03-05 09:25 | Done
293 | 2026-03-05 07:26 | 99 | M-5,7 | INV-02 | DC overvoltage | The O&M team performed a hard reset, and the module came back online. | 2026-03-05 09:20 | Done
294 | 2026-03-05 07:24 | 5 | M-1,2 | INV-01 | DC overvoltage | The O&M team performed a hard reset, and the module came back online. | 2026-03-05 09:44 | Done
295 | 2026-03-07 08:39 | 108 | M-2 | INV-01 | GFDI Protection | Inv 1 module 2 resistor and fuse replaced and inverter normalised. | 2026-03-07 12:26 | Done
296 | 2026-03-07 11:19 | 128 | INV-01 | INV-01 | 24 h insulation fault | The O&M team performed a hard reset, and the inverter came back online. | 2026-03-07 11:32 | Done
297 | 2026-03-09 06:36 | 30 | Module-5 | INV-02 | Access protection fault | The O&M team performed a hard reset, and the inverter came back online. | 2026-03-09 06:52 | Done
298 | 2026-03-10 | 108 | M-2 | INV-01 | GFDI Protection | Inv 1 module 2 resistor and fuse replaced and inverter normalised. | 2026-03-11 | Done

## Strings & PV Modules
Total |  | 270
Rectified |  | 270
Pending |  | 0
S. No | Date | BLOCK | SCB No | String No | Action Taken | Rectification Date | Status | Remarks
1 | 21-11-2025 | 2 | 35 | 15 | MC4 change | 25-11-2025 | Done
2 | 21-11-2025 | 3 | 3 | 5 | MC4 change | 27-11-25 | Done
3 | 21-11-2025 | 8 | 30 | 10 | MC4 change | 27-11-25 | Done
4 | 21-11-2025 | 13 | 28 | 9 | Replaced | 2025-12-04 | Done | module damage
5 | 21-11-2025 | 17 | 27 | 12 | MC4 change | 24-11-2025 | Done
6 | 21-11-2025 | 25 | 20 | 16 | MC4 change | 26-11-25 | Done
7 | 21-11-2025 | 30 | 23 | 9 | Fuse replaced | 27-11-25 | Done
8 | 21-11-2025 | 32 | 18 | 15 | MC4 change | 26-11-2025 | Done | module damage
9 | 21-11-2025 | 34 | 10 | 11 | Fuse replaced | 26-11-2025 | Done
10 | 21-11-2025 | 34 | 32 | 9 | MC4 change | 26-11-2025 | Done | module damage
11 | 21-11-2025 | 36 | 16 | 9 | Replaced | 2025-12-05 | Done | Wrong module Installed
12 | 21-11-2025 | 41 | 23 | 7 | Fuse replaced | 26-11-2025 | Done
13 | 21-11-2025 | 43 | 29 | 9 | change module direction | 2025-12-06 | Done | Wrong module Installed
14 | 21-11-2025 | 46 | 17 | 13 | Fuse replaced | 26-11-2025 | Done
15 | 21-11-2025 | 46 | 23 | 1 | Fuse replaced | 26-11-2025 | Done
16 | 21-11-2025 | 47 | 27 | 11 | Fuse replaced | 26-11-2025 | Done
17 | 21-11-2025 | 47 | 32 | 5 | Replaced | 2025-12-04 | Done | Wrong module Installed
18 | 21-11-2025 | 52 | 24 | 6 | Fuse replaced | 26-11-2025 | Done
19 | 21-11-2025 | 54 | 4 | 13 | Fuse replaced | 26-11-2025 | Done
20 | 21-11-2025 | 58 | 27 | 12 | MC4 change | 30-11-25 | Done
21 | 21-11-2025 | 66 | 16 | 1 | MC4 change | 30-11-25 | Done
22 | 21-11-2025 | 66 | 16 | 2 | MC4 change | 30-11-25 | Done
23 | 21-11-2025 | 67 | 3 | 9 | MC4 change | 30-11-25 | Done
24 | 21-11-2025 | 69 | 29 | 7 | MC4 change | 30-11-25 | Done
25 | 21-11-2025 | 72 | 3 | 16 | change module | 2025-08-12 | Done | Module damage
26 | 21-11-2025 | 73 | 2 | 3 | Replaced | 2025-12-04 | Done | Module damage
27 | 21-11-2025 | 78 | 22 | 4 | MC4 change | 30-11-25 | Done
28 | 21-11-2025 | 79 | 28 | 16 | MC4 change | 30-11-25 | Done
29 | 21-11-2025 | 80 | 1 | 8 | MC4 change | 27-11-25 | Done
30 | 21-11-2025 | 83 | 29 | 7 | MC4 change | 29-11-25 | Done
31 | 22-11-2025 | 83 | 30 | 3 | MC4 change | 29-11-25 | Done
32 | 22-11-2025 | 83 | 32 | 13 | MC4 change | 29-11-25 | Done
33 | 22-11-2025 | 84 | 1 | 4 | MC4 change | 27-11-25 | Done
34 | 22-11-2025 | 84 | 3 | 3 | MC4 change | 27-11-25 | Done
35 | 22-11-2025 | 84 | 3 | 15 | MC4 change | 27-11-25 | Done
36 | 22-11-2025 | 84 | 3 | 16 | MC4 change | 27-11-25 | Done
37 | 22-11-2025 | 84 | 32 | 2 | MC4 change | 27-11-25 | Done
38 | 22-11-2025 | 85 | 9 | 9 | Replaced | 2025-12-04 | Done | Module damage
39 | 22-11-2025 | 85 | 10 | 2 | MC4 change | 27-11-25 | Done
40 | 23-11-2025 | 85 | 35 | 6 | MC4 change | 27-11-25 | Done
41 | 23-11-2025 | 86 | 1 | 6 | MC4 change | 27-11-25 | Done
42 | 23-11-2025 | 86 | 9 | 9 | MC4 change | 27-11-25 | Done
43 | 23-11-2025 | 86 | 14 | 10 | MC4 change | 27-11-25 | Done
44 | 23-11-2025 | 87 | 22 | 15 | MC4 change | 27-11-25 | Done
45 | 23-11-2025 | 42 | 34 | 16 | Tracker issue rectifiy | 2025-12-06 | Done | Tracker issue
46 | 23-11-2025 | 88 | 11 | 2 | MC4 change | 27-11-25 | Done
47 | 23-11-2025 | 88 | 23 | 2 | MC4 change | 27-11-25 | Done
48 | 23-11-2025 | 94 | 1 | 4 | MC4 change | 27-11-25 | Done
49 | 23-11-2025 | 95 | 1 | 2 | MC4 change | 27-11-25 | Done
50 | 23-11-2025 | 95 | 1 | 3 | MC4 change | 27-11-25 | Done
51 | 23-11-2025 | 95 | 1 | 4 | MC4 change | 27-11-25 | Done
52 | 24-11-2025 | 95 | 1 | 5 | MC4 change | 27-11-25 | Done
53 | 24-11-2025 | 95 | 16 | 16 | MC4 change | 27-11-25 | Done
54 | 24-11-2025 | 97 | 28 | 2 | Rectified | 2025-12-04 | Done | wrong module installed
55 | 24-11-2025 | 98 | 34 | 10 | MC4 change | 27-11-25 | Done
56 | 24-11-2025 | 99 | 14 | 1 | MC4 change | 27-11-25 | Done
57 | 24-11-2025 | 99 | 25 | 4 | MC4 change | 27-11-25 | Done
58 | 24-11-2025 | 99 | 26 | 16 | MC4 change | 27-11-25 | Done
59 | 24-11-2025 | 102 | 16 | 1 | MC4 change | 27-11-25 | Done
60 | 24-11-2025 | 104 | 25 | 16 | MC4 change | 27-11-25 | Done
61 | 24-11-2025 | 104 | 36 | 11 | Replaced | 2025-06-12 | Done | wrong module installed
62 | 25-11-2025 | 106 | 24 | 11 | MC4 change | 27-11-25 | Done
63 | 25-11-2025 | 106 | 27 | 11 | MC4 change | 27-11-25 | Done
64 | 25-11-2025 | 106 | 28 | 15 | MC4 change | 27-11-25 | Done
65 | 25-11-2025 | 106 | 35 | 12 | MC4 change | 27-11-25 | Done
66 | 25-11-2025 | 107 | 16 | 4 | module have low voltage | 2025-09-12 | Done | module have low voltage
67 | 25-11-2025 | 108 | 8 | 12 | module change | 2025-12-06 | Done | Module damage
68 | 25-11-2025 | 109 | 17 | 6 | MC4 change | 27-11-25 | Done
69 | 25-11-2025 | 109 | 32 | 8 | MC4 change | 27-11-25 | Done
70 | 25-11-2025 | 116 | 24 | 7 | MC4 change | 27-11-25 | Done
71 | 25-11-2025 | 116 | 24 | 8 | MC4 change | 27-11-25 | Done
72 | 25-11-2025 | 120 | 23 | 3 | MC4 change | 27-11-25 | Done
73 | 25-11-2025 | 120 | 23 | 15 | MC4 change | 27-11-25 | Done
74 | 25-11-2025 | 120 | 23 | 16 | MC4 change | 27-11-25 | Done
75 | 26-11-2025 | 121 | 5 | 9 | MC4 change | 27-11-25 | Done
76 | 26-11-2025 | 121 | 7 | 5 | MC4 change | 27-11-25 | Done
77 | 26-11-2025 | 121 | 9 | 2 | MC4 change | 27-11-25 | Done
78 | 26-11-2025 | 124 | 17 | 4 | MC4 change | 28-11-25 | Done
79 | 26-11-2025 | 126 | 13 | 5 | MC4 change | 28-11-25 | Done
80 | 26-11-2025 | 126 | 26 | 16 | MC4 change | 28-11-25 | Done
81 | 26-11-2025 | 128 | 4 | 16 | MC4 change | 28-11-25 | Done
82 | 27-11-2025 | 128 | 34 | 11 | MC4 change | 28-11-25 | Done
83 | 27-11-2025 | 128 | 36 | 8 | MC4 change | 28-11-25 | Done
84 | 27-11-2025 | 130 | 8 | 16 | MC4 change | 28-11-25 | Done
85 | 27-11-2025 | 130 | 10 | 1 | MC4 change | 29-11-25 | Done
86 | 27-11-2025 | 130 | 24 | 7 | MC4 change | 29-11-25 | Done
87 | 27-11-2025 | 132 | 5 | 12 | MC4 change | 29-11-25 | Done
88 | 28-11-2025 | 47 | 27 | 16 | MC4 change | 29-11-25 | Done
89 | 28-11-2025 | 84 | 3 | 2 | MC4 change | 29-11-25 | Done
90 | 29-11-2025 | 99 | 16 | 11 | MC4 change | 29-11-25 | Done
91 | 29-11-2025 | 99 | 26 | 15 | MC4 change | 29-11-25 | Done
92 | 29-11-2025 | 101 | 3 | 1 | replaced | 2025-12-04 | Done | module damage
93 | 30-11-2025 | 102 | 15 | 1 | MC4 change | 30-11-25 | Done
94 | 30-11-2025 | 67 | 11 | 2 | MC4 change | 30-11-25 | Done
95 | 30-11-2025 | 28 | 23 | 14 | MC4 change | 30-11-25 | Done
96 | 30-11-2025 | 132 | 5 | 7 | MC4 change | 30-11-25 | Done
97 | 30-11-2025 | 80 | 1 | 5 | MC4 change | 30-11-25 | Done
98 | 30-11-2025 | 80 | 5 | 4 | MC4 change | 30-11-25 | Done
99 | 30-11-2025 | 120 | 17 | 15 | MC4 change | 2025-12-02 | Done
100 | 30-11-2025 | 121 | 7 | 10 | MC4 change | 2025-12-02 | Done
101 | 2025-01-12 | 8 | 17 | 16 | MC4 change | 2025-12-02 | Done
102 | 2025-01-12 | 13 | 28 | 9 | Change module | 2025-12-02 | Done | module damage
103 | 2025-01-12 | 17 | 27 | 7 | string voltage ok and in progress | 2025-07-12 | Done | 11 modules have low voltage in one string
104 | 2025-01-12 | 42 | 33 | 16 | Fuse replaced | 2025-12-02 | Done
105 | 2025-01-12 | 42 | 33 | 16 | MC4 Change | 2025-12-04 | Done
106 | 2025-02-12 | 53 | 34 | 3 | MC4 Change | 2025-12-04 | Done
107 | 2025-02-12 | 58 | 3 | 14 | MC4 Change | 2025-12-04 | Done
108 | 2025-02-12 | 59 | 16 | 1 | MC4 Change | 2025-12-04 | Done
109 | 2025-03-12 | 108 | 12 | 12 | Replaced | 2025-12-04 | Done | module damage
110 | 2025-03-12 | 125 | 16 | 9 | Replaced | 2025-12-04 | Done | module damage
111 | 2025-03-12 | 125 | 17 | 1 | Fuse replaced | 2025-12-02 | Done
112 | 2025-03-12 | 132 | 1 | 2 | Fuse replaced | 2025-12-02 | Done
113 | 2025-12-04 | 42 | 34 | 8 | MC4 Change | 2025-12-04 | Done
114 | 2025-12-04 | 53 | 13 | 13 | MC4 Change | 2025-12-04 | Done
115 | 2025-12-04 | 67 | 7 | 16 | MC4 Change | 2025-12-04 | Done
116 | 2025-12-04 | 107 | 16 | 3 | Fuse replaced | 2025-12-04 | Done
117 | 2025-12-05 | 53 | 15 | 13 | MC4 open/ Close MC4 | 2025-08-12 | Done
118 | 2025-12-06 | 83 | 27 | 3 | Rectified | 2025-12-06 | Done
119 | 2025-12-06 | 83 | 27 | 2 | Rectified | 2025-12-06 | Done
120 | 2025-12-06 | 83 | 27 | 1 | Rectified | 2025-12-06 | Done
121 | 2025-12-07 | 33 | 19 | 1 | MC4 open/ Close MC4 | 2025-08-12 | Done
122 | 2025-12-07 | 43 | 10 | 8 | MC4 open/ Close MC4 | 2025-08-12 | Done
123 | 2025-12-07 | 53 | 28 | 11 | MC4 open/ Close MC4 | 2025-08-12 | Done
124 | 2025-12-07 | 93 | 28 | 5 | MC4 close | 2025-09-12 | Done
125 | 2025-12-07 | 93 | 33 | 12 | MC4 close | 2025-09-12 | Done
126 | 2025-12-07 | 94 | 28 | 15 | Module change | 18-12-2025 | Done | Module Damage
127 | 2025-12-07 | 104 | 1 | 1 | MC4 Close | 2025-12-10 | Done
128 | 2025-12-07 | 104 | 36 | 11 | module direction change | 13-12-2025 | Done
129 | 2025-12-07 | 122 | 13 | 9 | MC4 open/ Close MC4 | 2025-08-12 | Done
130 | 2025-12-07 | 122 | 16 | 1 | MC4 open/ Close MC4 | 2025-08-12 | Done
131 | 2025-12-08 | 33 | 1 | 1 | MC4 open/ Close MC4 | 2025-08-12 | Done
132 | 2025-12-08 | 93 | 29 | 2 | MC4 close | 2025-09-12 | Done
133 | 2025-09-12 | 26 | 16 | 16 | MC4 close | 2025-09-12 | Done
134 | 2025-09-12 | 29 | 34 | 12 | MC4 close | 2025-09-12 | Done
135 | 2025-09-12 | 29 | 36 | 4 | MC4 close | 2025-09-12 | Done
136 | 2025-09-12 | 35 | 26 | 13 | MC4 close | 13-12-2025 | Done
137 | 2025-09-12 | 58 | 1 | 6 | MC4 close | 13-12-2025 | Done
138 | 2025-10-12 | 4 | 17 | 13 | MC4 Close | 2025-10-12 | Done
139 | 2025-10-12 | 11 | 33 | 13 | MC4 Close | 2025-10-12 | Done
140 | 2025-10-12 | 11 | 33 | 14 | MC4 Close | 2025-10-12 | Done
141 | 2025-10-12 | 11 | 33 | 15 | MC4 Close | 2025-10-12 | Done
142 | 2025-10-12 | 11 | 33 | 16 | MC4 Close | 2025-10-12 | Done
143 | 2025-10-12 | 26 | 16 | 16 | Replaced | 2025-12-31 | Done | module damage
144 | 2025-10-12 | 59 | 12 | 12 | MC4 Close | 2025-10-12 | Done
145 | 2025-10-12 | 126 | 5 | 16 | Module change | 18-12-2025 | Done | in progress
146 | 2025-11-12 | 36 | 11 | 3 | MC4 change | 13-12-2025 | Done
147 | 2025-11-12 | 17 | 27 | 7 | MC4 Close | 2025-11-12 | Done
148 | 2025-11-12 | 53 | 10 | 8 | MC4 Close | 13-12-2025 | Done
149 | 2025-11-12 | 59 | 25 | 12 | fuse fixed | 13-12-2025 | Done
150 | 2025-11-12 | 105 | 32 | 12 | MC4 change | 2025-12-12 | Done
151 | 2025-11-12 | 107 | 16 | 3 | Modules change | 14-12-2025 | Done | 7 Module are low voltage
152 | 2025-12-12 | 17 | 27 | 7 | module change | 13-12-2025 | Done
153 | 2025-12-12 | 42 | 28 | 13 | MC4 close | 14-12-20250 | Done
154 | 2025-12-12 | 107 | 16 | 4 | module change | 13-12-2025 | Done
155 | 13-12-2025 | 108 | 3 | 1 | change wire | 29-12-2025 | Done | Wire issue
156 | 14-12-2025 | 17 | 27 | 6 | On site ok | 14-12-2025 | Done
157 | 14-12-2025 | 35 | 26 | 13 | module change | 23-12-2025 | Done | 5 Module are low voltage
158 | 14-12-2025 | 41 | 23 | 7 | change pv module | 17-12-2025 | Done | 5 Module are low voltage
159 | 14-12-2025 | 107 | 16 | 7 | Modules change | 14-12-2025 | Done | 5 Module are low voltage
160 | 15-12-2025 | 20 | 29 | 7 | change MC4 | 15-12-2025 | Done
161 | 15-12-2025 | 26 | 30 | 16 | change MC4 | 15-12-2025 | Done
162 | 15-12-2025 | 67 | 11 | 2 | change MC4 | 15-12-2025 | Done
163 | 15-12-2025 | 121 | 15 | 7 | MC4 close | 15-12-2025 | Done
164 | 16-12-2025 | 30 | 19 | 4 | MC4 close | 16-12-2025 | Done
165 | 16-12-2025 | 56 | 8 | 13 | Change wrie | 16-12-2025 | Done
166 | 16-12-2025 | 56 | 8 | 14 | Change module | 17-12-2025 | Done
167 | 16-12-2025 | 56 | 8 | 15 | Change wrie | 16-12-2025 | Done
168 | 16-12-2025 | 56 | 8 | 16 | Change wrie | 16-12-2025 | Done
169 | 16-12-2025 | 58 | 23 | 14 | Module Replaced | 2025-12-28 | Done | module issue
170 | 17-12-2025 | 60 | 18 | 7 | MC4 change | 17-12-2025 | Done
171 | 17-12-2025 | 97 | 19 | 2 | MC4 change | 17-12-2025 | Done
172 | 17-12-2025 | 103 | 23 | 16 | MC4 Close | 17-12-2025 | Done
173 | 17-12-2025 | 123 | 1 | 10 | Change MC4 | 17-12-2025 | Done
174 | 17-12-2025 | 123 | 27 | 5 | Change MC4 | 17-12-2025 | Done
175 | 17-12-2025 | 125 | 20 | 1 | MC4 close | 17-12-2025 | Done
176 | 18-12-2025 | 41 | 23 | 7 | MC4 close | 18-12-2025 | Done
177 | 18-12-2025 | 56 | 8 | 14 | MC4 close | 18-12-2025 | Done
178 | 19-12-2025 | 4 | 12 | String-5 | on filed ok | 19-12-2025 | Done
179 | 19-12-2025 | 9 | 7 | String-5 | on filed ok | 19-12-2025 | Done
180 | 19-12-2025 | 52 | 29 | String-1 | on filed ok | 19-12-2025 | Done
181 | 19-12-2025 | 56 | 36 | String-3 | on filed ok | 19-12-2025 | Done
182 | 19-12-2025 | 73 | 19 | String-3 | on filed ok | 19-12-2025 | Done
183 | 19-12-2025 | 119 | 31 | String-7 | on filed ok | 19-12-2025 | Done
184 | 19-12-2025 | 122 | 25 | String-2 | on filed ok | 19-12-2025 | Done
185 | 20-12-2025 | 19 | 7 | 2 | on filed ok | 20-12-205 | Done
186 | 20-12-2025 | 20 | 3 | 16 | on filed ok | 20-12-205 | Done
187 | 20-12-2025 | 20 | 29 | 7 | on filed ok | 20-12-205 | Done
188 | 20-12-2025 | 28 | 23 | 14 | on filed ok | 20-12-205 | Done
189 | 20-12-2025 | 35 | 14 | 1 | on filed ok | 20-12-205 | Done
190 | 20-12-2025 | 36 | 2 | 3 | on filed ok | 20-12-205 | Done
191 | 20-12-2025 | 41 | 7 | 1 | on filed ok | 20-12-205 | Done
192 | 20-12-2025 | 41 | 7 | 6 | on filed ok | 20-12-205 | Done
193 | 20-12-2025 | 41 | 21 | 5 | on filed ok | 20-12-205 | Done
194 | 20-12-2025 | 41 | 23 | 3 | on filed ok | 20-12-205 | Done
195 | 20-12-2025 | 41 | 23 | 4 | on filed ok | 20-12-205 | Done
196 | 20-12-2025 | 43 | 1 | 16 | on filed ok | 20-12-205 | Done
197 | 20-12-2025 | 44 | 17 | 10 | on filed ok | 20-12-205 | Done
198 | 20-12-2025 | 44 | 30 | 6 | on filed ok | 20-12-205 | Done
199 | 20-12-2025 | 44 | 30 | 7 | on filed ok | 20-12-205 | Done
200 | 20-12-2025 | 48 | 5 | 10 | on filed ok | 20-12-205 | Done
201 | 20-12-2025 | 50 | 32 | 12 | on filed ok | 20-12-205 | Done
202 | 20-12-2025 | 51 | 27 | 6 | on filed ok | 20-12-205 | Done
203 | 20-12-2025 | 68 | 8 | 6 | on filed ok | 20-12-205 | Done
204 | 20-12-2025 | 97 | 19 | 2 | on filed ok | 20-12-205 | Done
205 | 20-12-2025 | 99 | 23 | 11 | on filed ok | 20-12-205 | Done
206 | 20-12-2025 | 107 | 14 | 14 | on filed ok | 20-12-205 | Done
207 | 20-12-2025 | 108 | 3 | 1 | on filed ok | 20-12-205 | Done
208 | 20-12-2025 | 119 | 32 | 1 | on filed ok | 20-12-205 | Done
209 | 20-12-2025 | 123 | 1 | 10 | on filed ok | 20-12-205 | Done
210 | 20-12-2025 | 124 | 4 | 11 | on filed ok | 20-12-205 | Done
211 | 22-12-2025 | 4 | 17 | 13 | modules no recitiy | 23-12-2025 | Done | 28 panels
212 | 22-12-2025 | 4 | 17 | 14 | modules no recitiy | 23-12-2025 | Done | 30 panels
213 | 22-12-2025 | 41 | 22 | 12 | on field ok | 23-12-2025 | Done
214 | 22-12-2025 | 41 | 23 | 3 | Replaced | 2025-12-27 | Done | Low voltage 3 module Low voltage:
215 | 22-12-2025 | 41 | 23 | 4 | Replaced | 2025-12-27 | Done | Low voltage :2 module Low voltage
216 | 22-12-2025 | 41 | 21 | 5 | on SCADA ok | 23-12-2025 | Done
217 | 22-12-2025 | 28 | 23 | 14 | on field ok | 23-12-2025 | Done
218 | 22-12-2025 | 96 | 17 | 8 | on SCADA ok | 23-12-2025 | Done
219 | 22-12-2025 | 123 | 1 | 10 | on SCADA ok | 23-12-2025 | Done
220 | 22-12-2025 | 126 | 5 | 16 | Replaced | 25-12-2025 | Done | Modules issue
221 | 22-12-2025 | 36 | 2 | 3 | on SCADA ok | 23-12-2025 | Done
222 | 22-12-2025 | 41 | 7 | 6 | Replaced | 27-12-25 | Done | one module low voltage
223 | 23-12-2025 | 43 | 1 | 16 | on field ok | 23-12-2025 | Done
224 | 23-12-2025 | 123 | 35 | 1 | on field ok | 23-12-2025 | Done
225 | 23-12-2025 | 123 | 35 | 2 | on field ok | 23-12-2025 | Done
226 | 23-12-2025 | 123 | 35 | 3 | on field ok | 23-12-2025 | Done
227 | 23-12-2025 | 117 | 8 | 4 | control box GFDI recitify | 23-12-2025 | Done
228 | 24-12-2025 | 38 | 9 | 6 | MC4 change | 24-12-2025 | Done
229 | 24-12-2025 | 41 | 7 | 1 | MC4 close | 24-12-2025 | Done
230 | 24-12-2025 | 41 | 7 | 4 | MC4 change | 24-12-2025 | Done
231 | 24-12-2025 | 41 | 21 | 8 | MC4 change | 24-12-2025 | Done
232 | 24-12-2025 | 65 | 10 | 10 | MC4 change | 24-12-2025 | Done
233 | 26-12-2025 | 65 | 7 | 10 | Replaced | 2026-01-01 | Done | module damage
234 | 26-12-2025 | 78 | 16 | 11 | Change Module | 29-12-2025 | Done | module damage
235 | 29-12-2025 | 35 | 10 | 2 | Replaced | 2026-01-01 | Done | module damage
236 | 30-12-2025 | 26 | 16 | 13 | Rectified | 2025-12-31 | Done | low current due tracker issue
237 | 30-12-2025 | 26 | 16 | 14 | Rectified | 2025-12-31 | Done | low current due tracker issue
238 | 30-12-2025 | 26 | 16 | 15 | Rectified | 2025-12-31 | Done | low current due tracker issue
239 | 2026-03-01 | 50 | 27 | 9 | Rectified | 2026-03-01 | Done | Module MC4 connected
240 | 2026-03-01 | 50 | 27 | 12 | Rectified | 2026-03-01 | Done | Module MC4 connected
241 | 2026-05-01 | 7 | 10 | 3 | Isolated | 2026-05-01 | Done | Ground Fault
242 | 2026-05-01 | 56 | 19 | 13 | Isolated | 2026-05-01 | Done | Ground Fault
243 | 2026-05-01 | 56 | 19 | 14 | Isolated | 2026-05-01 | Done | Ground Fault
244 | 2026-05-01 | 56 | 19 | 15 | Isolated | 2026-05-01 | Done | Ground Fault
245 | 2026-05-01 | 56 | 19 | 16 | Isolated | 2026-05-01 | Done | Ground Fault
246 | 2026-06-01 | 120 | 17 | 12 | MC4 Loose | 2026-06-01 | Done
247 | 2026-01-10 | 55 | 10 | 2 | Found OK on site | 2026-01-10 | Done
248 | 2026-01-11 | 124 | 17 | 2 | module damage | 2026-01-13 | Done
249 | 2026-01-14 | 132 | 5 | 15 | MC4 damage | 2026-01-15 | Done
250 | 2026-01-14 | 35 | 21 | 3 | MC4 damage | 2026-01-15 | Done
251 | 2026-01-24 | 38 | 9 | 6 | MC4 damage | 2026-01-25 | Done
252 | 2026-01-25 | 55 | 7 | 4 | Show zero on SCADA | 2026-01-25 | Done | ON field Found OK
253 | 2026-01-25 | 55 | 10 | 2 | Show zero on SCADA | 2026-01-25 | Done | ON field Found OK
254 | 2026-01-26 | 47 | 8 | 12 | MC4 Damage | 2026-01-27 | Done
255 | 2026-01-26 | 19 | 7 | 2 | Show zero on SCADA | 2026-01-26 | Done | ON field Found OK
256 | 2026-01-26 | 55 | 7 | 4 | Show zero on SCADA | 2026-01-26 | Done | ON field Found OK
257 | 2026-01-26 | 51 | 27 | 6 | 2 Module have less voltage | 2026-01-27 | Done
258 | 2026-01-26 | 60 | 30 | 6 | Show zero on SCADA | 2026-01-26 | Done | ON field Found OK
259 | 2026-01-26 | 76 | 13 | 15 | 4 Modules have less voltage | 2026-01-27 | Done
260 | 2026-01-26 | 39 | 17 | 10 | Show zero on SCADA | 2026-01-26 | Done | ON field Found OK
261 | 2026-01-30 | 110 | 9 | 7 | Show zero on SCADA | 2026-01-30 | Done | ON field Found OK
262 | 2026-01-30 | 34 | 14 | 1 | Insulation damage | 2026-02-01 | Done
263 | 2026-02-02 | 41 | 2 | 13 | String damage | 2026-02-05 | Done | MC4 Change
264 | 2026-02-03 | 7 | 33 | 3 | String damage | 2026-02-05 | Done | MC4 Change
265 | 2026-02-03 | 7 | 33 | 4 | String damage | 2026-02-05 | Done | MC4 Change
266 | 2026-02-07 | 108 | 3 | 1 | Insulation damage | 2026-02-08 | Done | Cable Change
267 | 2026-02-07 | 57 | 8 | 9 | Module Damage | 2026-02-08 | Done | Module Replaced
268 | 2026-02-09 | 50 | 26 | 11 | Show zero on SCADA | 2026-02-12 | Done | Tracker issue. Resolved
269 | 2026-02-20 | 44 | 2 | 14 | Show zero on SCADA | 2026-02-20 | Done | MC4 found open. Close the MC4
270 | 2026-02-25 | 83 | 18 | 5 | MC4 damage | 2026-02-25 | Done | MC4 replaced
271 | 2026-03-11 | 107 | 16 | 8 | Module damage |  |  | Three modules found faulty
272 | 2026-03-11 | 76 | 13 | 15 |  |  |  | Three modules found faulty,Low power

## PV Equipments Failure
ON Site Rectification
S.No | Date | Block | Equipment | Generation Affected | Issue | Action Taken | Done By | Rectification Date | Status | Spare Used | Old Serial Number | New Serial Number
1 | 2025-11-30 | 109 | MVPS | No | UPS Supply faulty | Replace UPS connector | O&M | 2025-12-02 | Done | No
2 | 2025-12-01 | 125 | MVPS | No | Winding temperature value not coming accurate on SCADA | Winding temperature board replaced | O&M | 2025-12-01 | Done | No
3 | 2025-12-07 | 77 | MVPS | Yes | R Phase Surge arrestor faulty | SPD Boot replaced | EPC/O&M | 2025-12-11 | Done | No
4 | 2025-12-08 | PV 63 | Cable | Yes | Joint failure | Replaced Joint | EPC/O&M | 2025-12-10 | Done | No
5 | 2025-12-09 | 32 | MVPS | No | Circuit breaker Closing coil not working | VCB Rectifier diode replaced | SG/O&M | 2025-12-18 | Done | No
6 | 2026-12-12 | PV 35 | Cable | Yes | Joint failure | Replaced Joint | EPC/O&M | 2025-12-13 | Done | No
7 | 2025-12-13 | 51 | Inverter | No | Inverter 2 Module 1 fan faulty | Replaced new fan | SG/O&M | 2025-12-13 | Done | Yes | AF185E3-075-000 | AF185E3-075-000
8 | 2025-12-13 | 120 | MVPS | NO | Minor oil Seepage | Replace gaskit | SG/O&M | 2025-12-14 | Done | No
9 | 2025-12-19 | 42 | WMS | NO | All sensor fan running continously | Put fan to auto mode | O&M | 2025-12-21 | Done | No
10 | 2025-12-19 | 59 | MVPS | NO | Winding temperature value not coming accurate on SCADA | Calibrated | SG/O&M | 2025-12-19 | Done | No
11 | 2025-12-28 | 122 | Inverter | No | Module 2 Spoiler fan faulty | Replaced new fan | SG/O&M | 2025-12-28 | Done | Yes | 820000039_ES000202_241202_2484 | 8200000339_ES000202_231129_1458
12 | 2026-01-02 | 121 | Transformer | No | Winding temperature 1 faulty | Replaced | SG/O&M | 2026-01-02 | Done | Yes | LD2408206093 | LD2502201349
13 | 2026-01-04 | PV 07(112) | Cable | Yes | Joint 1 Yellow phase faulty | Replaced | EPC/O&M | 2026-01-04 | Done | Yes
14 | 2026-01-05 | 49 | Transformer | No | Inverter 1 Module 4 AC Breaker misaligned | Rectified the breaker | SG/O&M | 2026-01-05 | Done | No
15 | 2026-01-08 | PV 11(113) | Cable | Yes | Joint 1 Blue phase faulty | Replaced | EPC/O&M | 2026-01-08 | Done | Yes
16 | 2026-01-10 | PV 11(113) | Cable | Yes | Joint 1 Yellow phase faulty | Replaced | EPC/O&M | 2026-01-10 | Done | Yes
17 | 2026-01-13 | PV 23(84) | Cable | Yes | Joint 1 Blue phase faulty | Replaced | EPC/O&M | 2026-01-14 | Done | Yes
18 | 2026-01-15 | PV 59 (55) | Cable | Yes | Joint 4 Yellow phase faulty | Replaced | EPC/O&M | 2026-01-15 | Done | No
19 | 2026-01-22 | PV 58 (107) | Cable | Yes | Blue phase J3 has fault | Replaced the joint | EPC/O&M | 2026-01-24 | Done | No
20 | 2026-01-22 | PV 15 (89) | Cable | Yes | Blue phase J2 Failure | Replaced the joint | EPC/O&M | 2026-01-25 | Done | No
21 | 2026-01-23 | 9 | Cable | No | CG1 Yellow phase Boot damage | Replaced the boot | EPC/O&M | 2026-01-23 | Done | No
22 | 2026-01-24 | PV 39 (59) | Cable | Yes | R phase J1 has fault | Replaced the joint | EPC/O&M | 2026-01-25 | Done | No
23 | 2026-01-24 | PV 41 (108) | Cable | Yes | R phase J3 has fault | Replaced the joint | EPC/O&M | 2026-01-25 | Done | No
24 | 2026-01-28 | PV 46 (60) | Cable | Yes | Yellow phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-01-29 | Done | No
25 | 2026-01-29 | PV 58 (107) | Cable | Yes | Blue Phse Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-01-29 | Done | No
26 | 2026-01-29 | PV 66 (83) | Cable | Yes | Red phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-01-29 | Done | No
27 | 2026-01-31 | PV 33 (111) | Cable | No | Red phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-01-31 | Done | No
28 | 2026-01-31 | PV 60 (78) | Cable | Yes | Blue phase joint 4 faulty | Replaced the joint | EPC/O&M | 2026-01-31 | Done | No
29 | 2026-02-01 | PV 41 (108) | Cable | Yes | Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-03 | Done | No
30 | 2026-02-02 | PV 58 (107) | Cable | Yes | Red phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-03 | Done | No
31 | 2026-02-02 | PV 49 (B34) | Cable | Yes | Red phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-03 | Done | No
32 | 2026-02-03 | PV 05 (B66) | Cable | Yes | Yellow phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-04 | Done | No
33 | 2026-02-03 | PV 42 (B11) | Cable | Yes | Blue phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-04 | Done | No
34 | 2026-02-03 | PV 59 (B55) | Cable | No | Yellow phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-04 | Done | No
35 | 2026-02-04 | PV 60 (B78) | Cable | Yes | Yellow Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-05 | Done | No
36 | 2026-02-04 | PV 05 (B74) | Cable | Yes | Red Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-06 | Done | No
37 | 2026-02-04 | PV 10 (B88) | Cable | Yes | Yellow phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-06 | Done | No
38 | 2026-02-04 | PV 02 (B116) | Cable | Yes | Blue phase Joint 6 faulty | Replaced the joint | EPC/O&M | 2026-02-06 | Done | No
39 | 2026-02-05 | PV 06 (B87) | Cable | Yes | Red Phase Joint 4 Faulty | Replaced the joint | EPC/O&M | 2026-02-06 | Done | No
40 | 2026-02-07 | PV 35 (B10) | Cable | Yes | Blue Phase joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-08 | Done | No
41 | 2026-02-07 | PV 48 (109) | Cable | Yes | Blue Phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-08 | Done | No
42 | 2026-02-10 | B110 | SCB | Yes | SCB 5 isolation switch damage | Replaced switch | EPC/O&M | 2026-02-11 | Done | Yes | 2443331082328PV3039A | 2443331078826PV3039A
43 | 2026-02-10 | PV 41(B108) | Cable | Yes | Red phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-11 | Done | No
44 | 2026-02-10 | PV 65 (98) | Cable | Yes | Blue Phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-11 | Done | No
45 | 2026-02-12 | PV 64 (B105) | Cable | Yes | Red phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-13 | Done | No
46 | 2026-02-13 | PV 64 (B105) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-14 | Done | No
47 | 2026-02-13 | PV 65 (98) | Cable | Yes | Blue Phase Joint 3 Faulty | Replaced the joint | EPC/O&M | 2026-02-14 | Done | No
48 | 2026-02-13 | PV 45 (B43) | Cable | Yes | Blue Phase joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-14 | Done | No
49 | 2026-02-14 | PV 23(B84) | Cable | Yes | Red Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-15 | Done | No
50 | 2026-02-14 | PV 56 (B57) | Cable | Yes | Yellow Phase Joint 4 Faulty | Replaced the joint | EPC/O&M | 2026-02-15 | Done | No
51 | 2026-02-14 | PV 46 (B60) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-16 | Done | No
52 | 2026-02-14 | PV 50 (B40) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-15 | Done | No
53 | 2026-02-15 | PV23 (B84) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-16 | Done | No
54 | 2026-02-15 | PV 30 (B45) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-18 | Done | No
55 | 2026-02-17 | PV 24 (B110) | Cable | Yes | Yellow Phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-18 | Done | No
56 | 2026-02-17 | PV 57 (B82) | Cable | Yes | Yellow Phase joint 5 faulty | Replaced the joint | EPC/O&M | 2026-02-18 | Done | No
57 | 2026-02-17 | PV 59 (B55) | Cable | Yes | Blue Phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-18 | Done | No
58 | 2026-02-18 | PV 42 (B11) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-19 | Done | No
59 | 2026-02-18 | PV 12 (B31) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
60 | 2026-02-18 | PV 28 (B20) | Cable | Yes | Blue Phase joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-19 | Done | No
61 | 2026-02-18 | PV 22 (B62) | Cable | Yes | Red Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-20 | Done | No
62 | 2026-02-18 | PV 58 (107) | Cable | Yes | Red Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-22 | Done | No
63 | 2026-02-18 | PV 60 (B78) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
64 | 2026-02-18 | PV 64 (B105) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
65 | 2026-02-18 | PV 65 (98) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
66 | 2026-02-18 | PV 66 (83) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
67 | 2026-02-19 | PV 47 (B80) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-22 | Done | No
68 | 2026-02-19 | PV 6 (B87) | Cable | Yes | Yellow Phase Joint 4 Faulty | Replaced the joint | EPC/O&M | 2026-02-20 | Done | No
69 | 2026-02-20 | PV 8 (B47) | Cable | Yes | Blue Phase Joint 3 Faulty | Replaced the joint | EPC/O&M | 2026-02-20 | Done | No
70 | 2026-02-20 | PV 44 (B30) | Cable | Yes | Yellow Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-22 | Done | No
71 | 2026-02-20 | PV 7 (B112) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-21 | Done | No
72 | 2026-02-21 | PV 51 (B61) | Cable | Yes | Red Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-23 | Done | No
73 | 2026-02-22 | PV 28 (B20) | Cable | Yes | Red Phase Joint 1 Faulty | Replaced the joint | EPC/O&M | 2026-02-23 | Done | No
74 | 2026-02-22 | PV 33 (111) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-24 | Done | No
75 | 2026-02-22 | PV 23(B84) | Cable | Yes | Red Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-23 | Done | No
76 | 2026-02-22 | PV 5 (B74) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-24 | Done | No
77 | 2026-02-22 | PV 7 (B112) | Cable | Yes | Red Phase Joint 1 and yellow phase joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-26 | Done | No
78 | 2026-02-23 | PV 57 (B82) | Cable | Yes | Red Phase Joint 1 Faulty | Replaced the joint | EPC/O&M | 2026-02-28 | Done | No
79 | 2026-02-23 | PV 64 (B105) | Cable | Yes | Blue Phase Joint 3 Faulty | Replaced the joint | EPC/O&M | 2026-02-28 | Done | No
80 | 2026-02-23 | PV 66 (83) | Cable | Yes | Yellow Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-25 | Done | No
81 | 2026-02-23 | PV 38 (B42) | Cable | Yes | Red Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-27 | Done | No
82 | 2026-02-23 | PV 43 (B19) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-25 | Done | No
83 | 2026-02-23 | PV 44 (B30) | Cable | Yes | Blue Phase Joint 2 faulty | Replaced the joint | EPC/O&M | 2026-02-27 | Done | No
84 | 2026-02-23 | PV 59 (B55) | Cable | Yes | Red Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-25 | Done | No
85 | 2026-02-23 | PV 63 (B77) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-25 | Done | No
86 | 2026-02-23 | PV 50 (B40) | Cable | Yes | Red Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-26 | Done | No
87 | 2026-02-23 | PV 53 (B106) | Cable | Yes | Yellow Phase Joint 4 Faulty | Replaced the joint | EPC/O&M | 2026-02-27 | Done | No
88 | 2026-02-23 | PV 47 (B80) | Cable | Yes | Yellow Phase Joint 1 faulty | Replaced the joint | EPC/O&M | 2026-02-28 | Done | No
89 | 2026-02-25 | PV 46 (B60) | Cable | Yes | Red Phase Joint 3 faulty | Replaced the joint | EPC/O&M | 2026-02-26 | Done | No
90 | 2026-02-28 | Block 42 | WMS | No | Communication Issue |  |  |  | Pending
91 | 2026-03-01 | PV 09 (B64) | Cable | Yes | Red Phase Joint 1 Faulty | Replaced the joint | EPC/O&M | 2026-03-02 | Done | No
92 | 2026-03-02 | PV 57 (B82) | Cable | Yes | Red Phase Joint 1 Faulty | Replaced the joint | EPC/O&M | 2026-03-03 | Done | No
93 | 2026-03-02 | PV 61 (B104) | Cable | Yes | Blue Phase Joint 2 Faulty | Replaced the joint | EPC/O&M | 2026-03-03 | Done | No
94 | 2026-03-08 | PV64(B105) | Cable | Yes | Blue Phase Joint 3-1 faulty | Replaced the joint | EPC/O&M | 2026-03-08 | Done
95 | 2026-03-12 | PV03 | Cable | Yes | Red phase J2-1 faulty | Replaced the joint | EPC/O&M | 2026-03-12 | Done

## SS Equipments failure
ON Site Rectification
S.No | Date | Area | Equipment | Generation Affected | Issue | Action Taken | Done By | Rectification Date | Status | Spare Used | Old Serial Number | New Serial Number
1 | 2026-01-01 | SUbstation | SVG 1 | No | Communication module faulty | Replaced | O&M | 2026-01-27 | Done | No | V1.06-00899 | V1.07-01541
2 | 2026-01-22 | Substation | SVG 2 | No | R phase termination faulty | New termination Done | EPC/O&M | 2026-01-23 | Done | No
3 | 2026-01-22 | Substation | SVG 1 | No | DC Unbalance fault | Replace A26 Module | EPC/O&M | 2026-01-27 | Done | Yes | 24AB042740025407 | 24A9002640025407
4 | 2026-01-22 | Substation | GT 1 | No | Oil seepage from winding temperature |  |  |  | Pending | No
5 | 2026-02-04 | Substation | SST 1 | No | HV Side termination faulty | HV side termination replaced | EPC/O&M | 2026-03-01 | Done | Yes
6 | 2026-02-05 | Substation | Transformer 4 | No | Due to high line voltage transformer trip | Reduce the voltage by using tap changer. Reset the alarm and transformer energize | O&M | 2026-02-05 | Done | No
7 | 2026-02-05 | Substation | Transformer 5 | No | Due to high line voltage transformer trip | Reduce the voltage by using tap changer. Reset the alarm and transformer energize | O&M | 2026-02-05 | Done | No
8 | 2026-02-05 | Substation | Transformer 6 | No | Due to high line voltage transformer trip | Reduce the voltage by using tap changer. Reset the alarm and transformer energize | O&M | 2026-02-05 | Done | No
9 | 2026-02-08 | Substation | Cameras | No | B015,20,123,126,25,29,33,43,61 cameras not working | After complete inspection found that fiber optic ports are swapped. So, restore the system after changing the ports and now all cameras are working | O&M | 2026-02-13 | Done | No
10 | 2026-02-17 | Substation | SVG 6 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-02 | Done | Yes
11 | 2026-02-19 | Substation | SVG 2 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-03 | Done | Yes
12 | 2026-02-23 | Substation | SVG 5 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-03 | Done | Yes
13 | 2026-02-25 | Substation | SVG 1 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-04 | Done | Yes
14 | 2026-02-27 | Substation | SVG 6 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-02 | Done | Yes
15 | 2026-03-05 | Substation | SVG 4 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-07 | Done | Yes
16 | 2026-03-08 | Substation | SVG 5 | No | DC Unbalance fault | Replaced the Module | O&M/OEM | 2026-03-10 | Done | Yes
17 | 2026-03-12 | Substation | SVG 6 | No | DC Unbalance fault |  | O&M/OEM
18
19
20
21
22
23
24
25
26

## SS Observations
S. No | Area | Equipment | Issue | Action Taken | Rectified Date | Status
1 | Substation | Earthing Transformer 1 | Silica gel not OK |  |  | Pending
2 | Substation | Earthing Transformer 2 | Silica gel not OK |  |  | Pending
3 | Substation | Earthing Transformer 3 | Silica gel not OK |  |  | Pending
4 | Substation | Earthing Transformer 4 | Silica gel not OK |  |  | Pending
5 | Substation | Earthing Transformer 5 | Silica gel not OK |  |  | Pending
6 | Substation | Earthing Transformer 6 | Silica gel not OK |  |  | Pending
7 | Substation | Auxiliary Transformer 1 | Silica gel not OK |  |  | Pending
8 | Substation | Auxiliary Transformer 2 | Silica gel not OK |  |  | Pending
9 | 110KV GIS | Line 2 | Earth switch name plate missing |  |  | Pending
10 | Protection Room | OHL 1 Protection Panel | Filter missing |  |  | Pending
11 | Protection Room | OHL 3 Protection Panel | Filter missing |  |  | Pending
12 | 33KV room | SVG 1 | Name Plate missing |  |  | Pending
13 | 33KV room | Interconnection Panel F.16 | Name Plate missing |  |  | Pending
14 | 33KV room | Interconnection Panel F.17 | Name Plate missing |  |  | Pending
15 | 33KV room | PV 20 | Name Plate missing |  |  | Pending
16 | 33KV room | Busbar Panel | Name Plate missing |  |  | Pending
17 | 33KV room | PV 21 | Name Plate missing |  |  | Pending
18 | 33KV room | SVG 2 | Name Plate missing |  |  | Pending
19 | 33KV room | Busbar Panel | Name Plate missing |  |  | Pending
20 | 33KV room | Interconnection Panel F.24 | Name Plate missing |  |  | Pending
21 | Pump Room | Fire system | Fire system power board fuse damage | Replaced | 2026-02-10 | DONE
22 | All Buildings | HVAC System | HVAC trip frquently |  |  | Pending
23 | Warehouse | Exhaust fan | Breaker trip when exhaust fan run | Rectified | 2025-12-21 | DONE
24 | O&M Building | Water Pump | Water Pump not working | Rectified | 2026-01-05 | DONE
25 | Pump Room | Water Valve | Water valve leakage | Tightened | 2025-12-22 | DONE
26 | Control Building | Water Pump | Water Pump not working | Rectified | 2026-01-05 | DONE
27 | Warehouse Building | Water Pump | Water Pump not working | Rectified | 2026-01-05 | DONE
28 | Pump Room | Fire fightning system | Diesel Pump signal is active | Rectified | 2026-01-07 | DONE
29 | GIS Room | Fire fightning system | Butterfly valve alarm coming | Rectified | 2026-02-02 | DONE
30 | Main gate | Hydraulic Pump | Road blocker not operational due to low hydraulic pump pressure | Rectified | 2026-01-31 | DONE
31 | Pump Room | Fire fightning Pump | Minor Leakage |  |  | Pending
32 | Server Room | CCTV Communication Switch | Switch PCB faulty | Replaced | 2026-01-08 | DONE
33 | ACDC Room | LVAC Drawyer | OGF to PACU1A Breaker not work | Rectified | 2026-02-25 | DONE

## PV Observations
[5 empty] | Date | 2026-03-04 | Prepared By | Ahmad Israr |  | 1st Cycle Observation | 168
[5 empty] | Block | ALL |  |  |  | Closed | 6
[5 empty] | Equipment | PV Field |  |  |  | Open | 163
Sr.No. | Date | BLOCK | Observation | Equipment | Description |  | Action need to Taken | Status | Rectification Date | Remarks
1 | 2025-08-21 | 125 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0 | 0
2 | 2025-08-23 | 121 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0 | 3
3 | 2025-08-23 | 124 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 3
4 | 2025-08-24 | 132 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0
5 | 2025-08-25 | 130 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0
6 | 2025-08-26 | 131 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0
7 | 2025-08-27 | 129 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open |  |  |  | 0
8 | 2025-08-28 | 128 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
9 | 2025-09-02 | 120 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
10 | 2025-09-03 | 119 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
11 | 2025-09-03 | 119 | Sealent Required | SCADA Box | Sealent need to add in cable entry points |  | Add Sealent | Open
12 | 2025-09-04 | 118 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
13 | 2025-09-04 | 118 | Sealent Required | SCADA Box | Sealent need to add in cable entry points |  | Add Sealent | Open
14 | 2025-09-06 | 117 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
15 | 2025-09-06 | 117 | Sealent Required | SCADA Box | Sealent need to add in cable entry points |  | Add Sealent | Open
16 | 2025-09-07 | 116 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
17 | 2025-09-08 | 115 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
18 | 2025-09-09 | 114 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
19 | 2025-09-10 | 113 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
20 | 2025-09-11 | 112 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
21 | 2025-09-13 | 111 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
22 | 2025-09-14 | 110 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
23 | 2025-09-15 | 109 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
24 | 2025-09-16 | 108 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
25 | 2025-09-17 | 107 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
26 | 2025-09-18 | 106 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
27 | 2025-09-20 | 105 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
28 | 2025-09-21 | 104 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
29 | 2025-09-22 | 103 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
30 | 2025-09-23 | 102 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
31 | 2025-09-24 | 100 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
32 | 2025-09-24 | 99 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
33 | 2025-09-25 | 98 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
34 | 2025-09-25 | 97 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
35 | 2025-09-25 | 96 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
36 | 2025-09-27 | 95 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
37 | 2025-09-27 | 94 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
38 | 2025-09-27 | 93 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
39 | 2025-09-27 | 92 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
40 | 2025-09-27 | 91 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
41 | 2025-09-28 | 90 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
42 | 2025-09-29 | 88 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
43 | 2025-09-29 | 87 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
44 | 2025-09-30 | 86 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
45 | 2025-09-30 | 85 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
46 | 2025-10-01 | 74 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
47 | 2025-10-01 | 66 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
48 | 2025-10-01 | 56 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
49 | 2025-10-02 | 75 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
50 | 2025-10-02 | 64 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
51 | 2025-10-02 | 47 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
52 | 2025-10-04 | 101 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
53 | 2025-10-05 | 89 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
54 | 2025-10-05 | 76 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
55 | 2025-10-05 | 65 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
56 | 2025-10-06 | 54 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
57 | 2025-10-06 | 46 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
58 | 2025-10-06 | 38 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
59 | 2025-10-07 | 31 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
60 | 2025-10-07 | 72 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
61 | 2025-10-07 | 62 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
62 | 2025-10-08 | 51 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
63 | 2025-10-08 | 44 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
64 | 2025-10-08 | 37 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
65 | 2025-10-11 | 27 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
66 | 2025-10-11 | 21 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
67 | 2025-10-11 | 17 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
68 | 2025-10-12 | 13 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
69 | 2025-10-12 | 9 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
70 | 2025-10-12 | 5 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
71 | 2025-10-13 | 2 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
72 | 2025-10-14 | 126 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
73 | 2025-10-15 | 73 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
74 | 2025-10-15 | 63 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
75 | 2025-10-16 | 52 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
76 | 2025-10-16 | 45 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
77 | 2025-10-18 | 35 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
78 | 2025-10-18 | 28 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
79 | 2025-10-19 | 24 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
80 | 2025-10-19 | 20 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
81 | 2025-10-20 | 15 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
82 | 2025-10-20 | 12 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
83 | 2025-11-06 | 127 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
84 | 2025-11-11 | 37 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
85 | 2025-11-11 | 44 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
86 | 2025-11-11 | 51 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
87 | 2025-11-11 | 62 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
88 | 2025-11-11 | 72 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
89 | 2025-11-12 | 2 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
90 | 2025-11-12 | 9 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
91 | 2025-11-12 | 13 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
92 | 2025-11-12 | 21 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
93 | 2025-11-12 | 125 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
94 | 2025-11-12 | 5 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
95 | 2025-11-12 | 17 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
96 | 2025-11-13 | 1 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
97 | 2025-11-13 | 3 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
98 | 2025-11-13 | 6 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
99 | 2025-11-13 | 8 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
100 | 2025-11-17 | 23 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
101 | 2025-11-18 | 29 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
102 | 2025-11-18 | 36 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
103 | 2025-11-18 | 42 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
104 | 2025-11-18 | 53 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
105 | 2025-11-18 | 59 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
106 | 2025-11-18 | 70 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
107 | 2025-11-18 | 79 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
108 | 2025-11-19 | 4 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
109 | 2025-11-19 | 11 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
110 | 2025-11-19 | 25 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
111 | 2025-11-20 | 19 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
112 | 2025-11-20 | 30 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
113 | 2025-11-20 | 33 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
114 | 2025-11-20 | 43 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
115 | 2025-11-20 | 48 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
116 | 2025-11-20 | 60 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
117 | 2025-11-24 | 16 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
118 | 2025-11-24 | 22 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
119 | 2025-11-24 | 26 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
120 | 2025-11-24 | 34 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
121 | 2025-11-23 | 40 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
122 | 2025-11-23 | 49 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
123 | 2025-11-23 | 61 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
124 | 2025-11-23 | 68 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
125 | 2025-11-22 | 71 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
126 | 2025-11-22 | 80 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
127 | 2025-11-23 | 81 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
128 | 2025-11-25 | 69 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
129 | 2025-11-25 | 82 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
130 | 2025-11-25 | 122 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
131 | 2025-11-24 | 27 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
132 | 2025-11-24 | 26 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
133 | 2025-11-24 | 124 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
134 | 2025-11-22 | 95 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
135 | 2025-11-22 | 71 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
136 | 2025-11-22 | 43 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
137 | 2025-11-20 | 48 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
138 | 2025-11-20 | 60 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
139 | 2025-11-26 | 32 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
140 | 2025-11-26 | 39 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
141 | 2025-11-26 | 41 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
142 | 2025-11-26 | 50 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
143 | 2025-11-26 | 55 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
144 | 2025-11-26 | 57 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
145 | 2025-11-26 | 67 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
146 | 2025-11-26 | 78 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
147 | 2025-11-26 | 1 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
148 | 2025-11-12 | 21 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
149 | 2025-11-27 | 96 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
150 | 2025-11-27 | 129 | Earthing Rod | RMU | Earthing Rod is missing in RMU |  | Need to add | Open
151 | 2025-11-27 | 7 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
152 | 2025-11-28 | 10 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
153 | 2025-11-28 | 14 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
154 | 2025-11-28 | 18 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
155 | 2025-11-29 | 58 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
156 | 2025-11-29 | 77 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
157 | 2025-11-29 | 83 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
158 | 2025-11-29 | 84 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
159 | 2025-11-29 | 123 | Silica gel not good | Transformer | Silica gel need to replace |  | Replaced | Open
160 | 2025-12-22 | 128 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
161 | 2025-12-22 | 103 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
162 | 2025-12-22 | 31 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
163 | 2025-12-22 | 40 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
164 | 2025-12-22 | 124 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
165 | 2025-12-22 | 60 | MVPS Lights | MVPS | MVPS lights are not working |  | Replaced | Close | 2026-01-21
166 | 2025-12-30 | PV Area | Fence Damage | Fence | Near Road 12 Fence Damage |  | Rectification | Open
167 | 2026-01-01 | PV Area | Housekeeping | PV Area | Housekeeping need to be done |  | Cleaning performed | Open
168 | 2026-01-01 | PV Area | Route markers damage | PV Area | Many route markers damaged |  | Replaced | Open
169 | 2026-03-09 | PV Area | Block-40 Tracker Box Door lock damage | PV Area | Block-40 Tracker Box Door lock damage |  |  | Open

## Documents
Maintenance Checklist
SNO | NAME | STATUS REVISION1 | STATUS REVISION2 | Responsible
1 | Weather Monitoring System Checklist | C4 | C2 | Ahmad Israr
2 | Power Station Checklist | C4 | C1 | Ahmad Israr
3 | Tracker Checklist | C4 | UR | Ahmad Israr
4 | Robot Checklist | C3 | UR | Farooq Ghumro
5 | PV Module Checklist | C3 | UR | Ahmad Israr
6 | Combiner Box Checklist | C3 | UR | Ahmad Israr
7 | BATTERY BANK CHECKLIST | C4 | UR | Ahmad Israr
8 | STATIC VAR GENERATOR CHECKLIST | C4 | Pending | Ahmad Israr
9 | POWER TRANSFORMER CHECKLIST | C4 | Pending | Ahmad Israr
10 | EARTHING TRANSFORMER CHECKLIST | C4 | Pending | Rahim
11 | 110 KV GIS MAINTENANCE CHECKLIST | C4 | Pending | Rahim
12 | 33KV MAINTENANCE CHECKLIST | C4 | Pending | Khalid
13 | LVAC PANEL CHECKLIST | C4 | Pending | Ahmad Israr
14 | UPS AND DC CHARGERS (110-DC, 48-DC,125-DC) CHECKLIST | C4 | UR | Farooq Ghumro
15 | SUBSTATION CONTROL & PROTECTION PANELS CHECKLIST | C4 | Pending | Ahmad Israr
16 | SUBSTATION DISTRIBUTION PANEL/BOARD (LIGHTING/POWER) CHECKLIST | C4 | Pending | Naveed
17 | HVAC SYSTEM CHECKLIST | Pending |  | Naveed
18 | EMERGENCY DIESEL GENERATOR CHECKLIST | C4 | Pending | Ahmad Israr
19 | FIRE FIGHTING SYSTEM CHECKLIST | Pending |  | HSE Team
20 | ALL FACILITIES LIGHTING AND POWER SYSTEM CHECKLIST | Pending |  | Ahmad Israr
21 | WATER PUMPING SYSTEM CHECKLIST | Pending |  | Ahmad Israr
22 | SURGE ARRESTOR CHECKLIST | C4 | Pending | Ahmad Israr
23 | AUXILIARY TRANSFORMER CHECKLIST | C4 | Pending | Rahim
24 | CCTV & ACCESS CONTROL CHECKLIST | Pending |  | Ahmad Israr
25 | PERIMETER LIGHTING SYSTEM CHECKLIST | C4 | Pending | Ahmad Israr
26 | MAIN GATE CHECKLIST | C4 | Pending | Ahmad Israr
27 | Communication System Checklist | Pending |  | Ahmad Israr
28 | PROCEDURE of_BATTERY BANK | C4 | UR | Ahmad Israr
29 | PROCEDURE of_STATIC VAR GENERATOR | C4 | Pending | Ahmad Israr
30 | PROCEDURE of_POWER TRANSFORMER | C4 | Pending | Ahmad Israr
31 | PROCEDURE of_EARTHING TRANSFORMER | C4 | Pending | Rahim
32 | PROCEDURE of_110 KV GIS MAINTENANCE | C4 | C2 | Rahim
33 | PROCEDURE of_33KV MAINTENANCE | C4 | Pending | Khalid
34 | PROCEDURE of_LVAC PANEL | C4 | Pending | Ahmad Israr
35 | PROCEDURE of_UPS AND DC CHARGERS (110-DC, 48-DC,125-DC) | C4 | UR | Farooq Ghumro
36 | PROCEDURE of_SUBSTATION CONTROL & PROTECTION PANELS | C4 | Pending | Ahmad Israr
37 | PROCEDURE of_SUBSTATION DISTRIBUTION PANEL/BOARD (LIGHTING/POWER) | C4 | Pending | Naveed
38 | PROCEDURE of_HVAC SYSTEM | Pending | Pending | Naveed
39 | PROCEDURE of_EMERGENCY DIESEL GENERATOR | C4 | Pending | Ahmad Israr
40 | PROCEDURE of_FIRE FIGHTING SYSTEM | Pending | Pending | HSE Team
41 | PROCEDURE of_ALL FACILITIES LIGHTING AND POWER SYSTEM | Pending | Pending | Ahmad Israr
42 | PROCEDURE of_WATER PUMPING SYSTEM | Pending | Pending | Ahmad Israr
43 | PROCEDURE of_SURGE ARRESTOR | C4 | Pending | Ahmad Israr
44 | Procedure of_AUXILIARY TRANSFORMER | C4 | Pending | Rahim
45 | Procedure of_COMMUNICATION SYSTEM | Pending | Pending | Ahmad Israr
46 | PROCEDURE of_WEATHER STATIONS | C4 | C2 | Ahmad Israr
47 | PROCEDURE of_POWER STATION | C4 | C2 | Ahmad Israr
48 | PROCEDURE of_TRACKERS | C4 | UR | Ahmad Israr
49 | PROCEDURE of_PV MODULES | C4 | UR | Ahmad Israr
50 | PROCEDURE of_COMBINER BOX | C4 | UR | Ahmad Israr
51 | Procedure of_CLEANING ROBOT | C4 | UR | Farooq Ghumro
52 | PROCEDURE of_CCTV & ACCESS CONTROL | Pending | Pending | Ahmad Israr
53 | PROCEDURE of_PERIMETER LIGHTING SYSTEM | Pending | Pending | Ahmad Israr
54 | PROCEDURE of_MAIN GATE | Pending | Pending | Ahmad Israr